## Schedule 1_SS
400/132kV MAKINDU SUBSTATION
Schedules of Rates and Prices
Schedule No. 1
Plant and Mandatory Spare Parts Supplied from Abroad
Item | Description | Unit | Qty | Unit Price |  | Total Price
|  |  |  | Foreign Currency | Local Currency (KSh) = KENYAN SHILLINGS | Foreign Currency | Local Currency (KSh) = KENYAN SHILLINGS
|  |  | (1) | (2) | (3) | (4)=(1)* (2) | (5)=(1)*(3)
Bidders shall enter a code representing the country of origin of all imported plant and equipment.
Specify currency create and use as many columns for unit price and total price as there are currencies
1 | 400kV PRIMARY PLANT
1.1 | Circuit breaker (1 Pole operated -3 phase) Complete with mechanism box , Central Control Panel, complete with operating platform. All accessories will be included to make testing and commissioning completed . | No. | 12
1.2 | Disconnector, motorized (1 Pole operated-3-phase) with earth mat, Complete with Central Control Panel. All accessories will be included to make testing and commissioning completed. | No. | 24
1.3 | Disconnector, motorized (1 Pole operated-3 phase) complete with one integral motorized earth switch and earth mat, Complete with Central Control Panel. All accessories will be included to make testing and commissioning completed. | No. | 8
1.4 | Surge arrester (1-phase) including surge counter with earth leakage meter connecting to earth grid. All accessories will be included to make testing and commissioning completed. | No. | 24
1.5 | Post insulator -for main busbar, All accessories will be included to make testing and commissioning completed | Lot | 1
1.6 | Post insulator - for bay busbar, All accessories will be included to make testing and commissioning completed | Lot | 1
1.7 | Post insulator - Under-hung All accessories will be included to make testing and commissioning completed | Lot | 1
1.8 | Strain (Longrod)insulator - with turnbuckle All accessories will be included to make testing and commissioning completed | Lot | 1
1.9 | Strain(Longrod) insulator - without turnbuckle All accessories will be included to make testing and commissioning completed. | Lot | 1
1.10 | Post type current transformer for Protection & Measuring (3 Core,1-phase) for lines. All accessories will be included to make testing and commissioning completed. Phase summation galvanized junction box will be provided. | No. | 24
1.11 | Post type current transformer for Protection & Measuring (3 Core,1-phase).for transformers All accessories will be included to make testing and commissioning completed. Phase summation galvanized junction box will be provided. | No. | 12
1.12 | Post type current transformer -High Accuracy Tariff metering (2 Core, 1-phase) All accessories will be included to make testing and commissioning completed. Phase summation galvanized junction box will be provided. | No. | 12
1.13 | Capacitive voltage transformer - (Protection & Measuring, 1-phase) Supply will be based on TDS and description. All accessories will be included to make testing and commissioning completed . Phase summation galvanized junction box will be provided | No. | 20
1.14 | Capacitive Voltage transformer (1-phase) (High Accuracy Metering) Supply will be based on TDS and description. All accessories will be included to make testing and commissioning completed. Phase summation galvanized junction box will be provided. | No. | 12
1.15 | Conductor - Tubular Supply will be based on TDS and description. All accessories will be included to make testing and commissioning completed. | Lot | 1
1.16 | Conductor - Stranded Supply will be based on TDS and description. All accessories will be included to make testing and commissioning completed. | Lot | 1
1.17 | Connectors - Tube ; All accessories will be included to make testing and commissioning completed | Lot | 1
1.18 | Connectors - for Stranded flashover, down-droppers, equipment connect.etc. All accessories will be included to make testing and commissioning completed | Lot | 1
TOTAL PRICE ITEM 1
2 | 132kV PRIMARY PLANT
2.1 | Circuit breaker (3 pole/gang operated, 3 phase) Complete with mechanism/central box ( IBT1 & 2, Bus sections ). All accessories will be included to make testing and commissioning completed, complete with operating platform. | No. | 4
2.2 | Circuit breaker (3 pole/gang operated, 3 phase) Complete with mechanism/central box (for bus coupler ). All accessories will be included to make testing and commissioning completed, complete with operating platform. | No. | 2
2.3 | Circuit breaker (1 pole operated-3 phases) for OHL Complete with mechanism box/Central Control Panel. All accessories will be included to make testing and commissioning completed complete with operating platform | No. | 2
2.4 | Disconnector, motorized (3-phase) with earth math connecting to earth grid(busbar DS for IBT1 & IBT 2 and OHL). All accessories will be included to make testing and commissioning completed | No. | 8
2.5 | Disconnector, motorized (3-phase) with earth math connecting to earth grid(for bus couplers). All accessories will be included to make testing and commissioning completed | No. | 4
2.6 | Disconnector, motorized (3-phase) complete with one integral earth switch(for IBT 1& IBT 2 and OHLs) All accessories will be included to make testing and commissioning completed. Earth mat will be provided connected to earth grid. | No. | 4
2.7 | Disconnector, motorized (3-phase) complete with two integral motorized earth switches(for bus sections) All accessories will be included to make testing and commissioning completed. Earth mat will be provided connected to earth grid. | No | 4
2.8 | Surge arrester (1-phase) including surge counter with earth leakage meter connecting to earth greed All accessories will be included to make testing and commissioning completed. | No. | 12
2.9 | Post insulator - for the main busbar, All accessories will be included to make testing and commissioning completed | Lot | 1
2.10 | Post insulator - for the bay busbar support, All accessories will be included to make testing and commissioning completed | Lot | 1
2.11 | Post insulator - Under-hung All accessories will be included to make testing and commissioning completed | Lot | 1
2.12 | Strain (Longrod) insulator - with turnbuckle All accessories will be included to make testing and commissioning completed | Lot | 1
2.13 | Strain (Longrod) insulator - without turnbuckle All accessories will be included to make testing and commissioning completed | Lot | 1
2.14 | 132kV Post type current transformer for IBT Protection & Metering. (1-phase, 4 cores) with galvanized phase summation junction box. All accessories will be included to make testing and commissioning completed | No. | 6
2.15 | 132kV Post type current transformer for OHL Protection & Metering. (1-phase, 4 cores) with galvanized phase summation junction box. All accessories will be included to make testing and commissioning completed | No. | 6
2.16 | 132kV Post type current transformer, for Bus section and bus coupler (1-phase, 2 cores) with galvanized phase summation junction box. All accessories will be included to make testing and commissioning completed | No. | 24
2.17 | 132kV Capacitive voltage Transformer of Protection & Measuring (1-phase, three cores) for 132kV busbar. All accessories will be included to make testing and commissioning completed. | No | 4
2.18 | 132kV Capacitive voltage transformer - (1-phase, High Accuracy Metering) for protection and metering with galvanized phase summation box. All accessories will be included to make testing and commissioning completed | No. | 12
2.19 | Conductor - Tube - 132kV Bus bar 1&2 - min. 100mm dia All accessories will be included to make testing and commissioning completed | Lot | 1
2.20 | Conductor - Stranded (overfly/down drop and equipment connection) All accessories will be included to make testing and commissioning completed | Lot | 1
2.21 | Connectors - Tube min. 100mm dia (132kv Bus bar) All accessories will be included to make testing and commissioning completed | Lot | 1
2.22 | Connectors - Stranded conductor All accessories will be included to make testing and commissioning completed | Lot | 1
2.23 | Low Power Instrument Transformer (LPIT),or Optical CT with all accessories necessary for complete testing and commissioning | No | 3
TOTAL PRICE ITEM 2
3 | Power Transformer and Busbar Reactor
3.1 | INTERBUS TRANSFORMER (IBT - Three windings)
3.1.1 | Three phase units with three windings 400/132/11kV, 75/90 MVA (ONAN/ONAF) including HV/LV/TV/Neutral CT's & Bushing CTs | No. | 2
3.1.2 | Fire Protection system with Nitrogen Injection & Oil Evacuation System, explosion proof, based on description in Tender document (all accessories including trolley fire extinguisher, sand box , shovels and buckets(at least 2 sets)shall be included to make testing and commissioning completed) | No. | 2
3.1.3 | Power transformer online monitoring system based on description in Tender document (all accessories will be included to make testing and commissioning completed). | No. | 2
3.1.4 | Parallel transformer online operation system using IEC 61850 GOOSE communication and interconnecting in master -follower mode (based on description on description in Tender document ), (all accessories will be included to make testing and commissioning completed). | Lot | 1
3.1.5 | Surge arrester (1-phase), installed in the Power TX11kV cable box | No. | 6
3.2 | Busbar Shunt Reactor
3.2.1 | Three phase units with three windings 400kV, 50MVAR Reactor including HV and Neutral CT's & Bushing CTs | No. | 2
TOTAL PRICE ITEM 3
4 | 400kV PROTECTION SYSTEMS
4.1 | 400kV OHL Protection System (4 sets)
4.1.1 | Main 1 21L Protection (different vendor from Main 2) | No. | 4
4.1.2 | Main 2 87L Protection (different vendor from Main 1) | No. | 4
4.1.3 | Auto-Reclose Protection function (included within Main 1 and Main2) | No. | 4
4.1.4 | Panels including all accessories, e.g. AC/DC system, wiring etc. to make the system complete | Panels (No) | 4
4.1.5 | Phasor Measurement Unit (PMU) including PDC, and accessories required to integrate in KETRACO's SDH network | Lot | 1
4.1.6 | Point on Wave controller | No. | 8
4.2 | 400kV HV Transformer Protection System including (2 sets):
4.2.1 | Main 87T+87N Protection | No. | 2
4.2.2 | Backup 50/51(N) Protection and HV Neutral 51N Stand-by Earth-Fault Protection | No. | 2
4.2.3 | 87HVC1 Connection Protection (different vendor from Main 87HVC2) | No. | 2
4.2.4 | 87HVC2 Connection Protection (different vendor from Main 87HVC1) | No. | 2
4.2.5 | Panels including all accessories, e.g. AC/DC system, wiring etc. to make the system complete | Panels (No) | 4
4.2.6 | Point on Wave controller | No. | 2
4.3 | 400kV HV Busbar Shunt Reactor including (2 sets):
4.3.1 | Main 87R+87NR Protection | No. | 2
4.3.2 | Backup 50/51(N) Protection | No. | 2
4.3.3 | 87HVC1 Connection Protection (different vendor from Main 87HVC2) | No. | 2
4.3.4 | 87HVC2 Connection Protection (different vendor from Main 87HVC1) | No. | 2
4.3.5 | Panels including all accessories, e.g. AC/DC system, wiring etc. to make the system complete | Panels (No) | 2
4.3.6 | Point on Wave controller | No. | 2
4.4 | 400kV Bus bar Protection System 400kV Bus bar Protection (BUS BAR 1 &2 ). All accessories will be included to make testing and commissioning completed. | Lot | 2
4.4.1 | The 50BF function shall be included for CBS as per SLDs | No | 8
4.5 | Modification works in remote substation Rabai or Mariakani & Isinya Substation. Including relay setting & relay configuration etc. | Lot | 1
4.6 | Miscellaneous modification works as necessary to make the complete 400kV protection system functional | Lot | 1
4.7 | Update the remote substations drawings (Rabai/Mariakani and Isinya) | Lot | 1
TOTAL PRICE ITEM 4
5 | 132kV PROTECTION SYSTEMS
5.1 | 132kV OHL Protection System including: | Lot | 2
5.1.1 | Main 1 21L Protection (different vendor from Main 2) | No. | 2
5.1.2 | Main 2 87L Protection (different vendor from Main 1) | No. | 2
5.1.3 | Auto-Reclose Protection function (included within Main 1 and Main2) | No. | 2
5.1.4 | Panels including all accessories, e.g. AC/DC system, wiring etc. to make the system complete | Panels (No) | 2
5.1.5 | Modification works at the remote end substations from Makindu substation including relay setting calculations & relay configuration & testing. | lot | 1
5.2 | 132kV LV Transformer Protection System including: | Lot | 2
5.2.1 | Backup 50/51(N),67/67N Protection, LV NEUTRAL, 51N, LV REF, LVSBEF | No. | 2
5.2.2 | Earthing Transformer 11kV side-87N/TV, 11kV side standby earth fault protection 51NTV, 50/51, TV REF and BCU | No. | 2
5.2.3 | The AVR Panel including all accessories including AVR, AVR relay, wiring etc. to make the system completes. (one panel for both) | Panels (No) | 2
5.2.4 | Panels including all accessories, e.g. AC/DC system, wiring etc. to make the system complete | Panels (No) | 2
5.3 | 132kV complete Bus bar Protection System - OHL Bus bar protections - TR bus bar protections - Bus coupler Bus bar protection - Bus section Bus bar protection - Bus bar panels | Lot | 1
5.4 | 132kV Protection - Bus coupler protection (integrated with BCU) - Bus section protection (integrated with BCU) - Bus coupler & Bus section shared panel | Lot | 2
5.5 | Miscellaneous modification works as necessary to make the complete 132kV protection system functional | Lot | 1
TOTAL PRICE ITEM 5
6 | 400/132kV SUBSTATION AUTOMATION SYSTEM
6.1 | 400/132kV Bay Control Units and panels: | Lot | 2
6.1.1 | Bay Control Units (BCU) 400kV (full diameters) - One BCU per CB. include 25 and VSL function - BCU for CB-Bus-OHL - BCU for CB-TIE include 50BF function - BCU for CB-Bus-Tx | Lot | 2
6.1.2 | Bay Control Units (BCU) 400kV (full diameters) - One BCU per CB. include 25 and VSL function - BCU for CB-Bus-OHL - BCU for CB-TIE include 50BF function - BCU for CB-Bus-Reactor | Lot | 2
6.1.3 | Bay Control Units (BCU) 132kV - One BCU per CB. include 25 and VSL function - BCU for OHL - BCU for Coupler (C&P combined ) - BCU for Bus-Section (C&P combined) - BCU for each Transformer feeder | Lot | 1
6.1.4 | Bay Control Panels - 400kV one panel per diameter - 132kV C&P combined in the same panel | Lot | 1
6.1.5 | Auxiliary and Common Services Bay Control Units BCUs, one per each Earthing Transformer 11/0.415kV, including 415V side-51N protection. Including one combined panel for both | Lot | 1
6.2 | 400/132kV Local Area Network: | Lot | 2
6.2.1 | PRP Process Bus Network composed of both LAN-A and LAN-B, 1000BaseFX, industrial Eth switches, PTP capable (technical requirements in Appendix), Physically independent thus: - PRP LAN A & LAN B, 400kV Diameter 1 - PRP LAN A & LAN B, 400kV Diameter 2 - PRP LAN A & LAN B, 400kV Diameter 3 - PRP LAN A & LAN B, 400kV Diameter 4 - PRP LAN A & LAN B, 132kV for two OHL bays - PRP LAN A & LAN B, 132kV for two Transformer bays - PRP LAN A & LAN B, 132kV for two couplers and two bus section bays Switches to be installed in the control cabinets of the corresponding bay | Lot | 1
6.2.2 | PRP Station Bus Network composed of both LAN-A and LAN-B, 100BaseFX, industrial Eth switches, PTP capable (technical requirements in Appendix) | Lot | 1
6.2.3 | PRP Process Bus Inter-bay Network composed of both LAN-A and LAN-B, 1000BaseFX, industrial Eth switches, PTP capable (technical requirements in Appendix), Physically independent thus | Lot | 1
6.2.4 | PRP Redboxes, 100BaseFX, PTP capable (technical requirements in Appendix), minimum 8 ports | Lot | 4
6.2.5 | RSTP DMZ Network, 100BaseTx, PTP capable (technical requirements in Appendix) | Lot | 1
6.2.6 | Outdoor armored Fiber optics and Fiber Optic Organizer for connections from the Marshaling Kiosks to the control room | Lot | 1
6.2.7 | Armed Fiber optics, patch cords FO, Patch cords Eth and other wiring necessary for the Network | Lot | 1
6.3 | Firewall: SSL/TSL/SSH/NAT, 6 ports, throughput 1.4 Gbps (technical requirements in Appendix) | Lot | 1
6.4 | Cybersecurity Intrution Detection and Functional Monitoring System | Lot | 2
6.5 | Human Machine Interface (OWS) | Lot | 2
6.6 | Engineering Workstation (EWS) | No. | 2
6.7 | SCADA servers | No. | 2
6.8 | Gateways | No. | 2
6.9 | Time synchronization system including clocks, antennas and accessories (see technical requirements in Digital substation Appendix) | No. | 2
6.10 | Laser Jet printer (A3 & A4) | No. | 1
6.11 | General Purpose Printer | No. | 1
6.12 | 400/132kV Digital interfaces: | Lot | 2
6.12.1 | Marshalling Kiosks for each 400kV Bus-side CB, including: - 3 MUs and their test terminal blocks - 2 SCUs - Fiber Optic Organizer - AC/DC and other Auxiliary systems Combination of MUs/SCUs are possible based on the Digital substation Appendix | Lot | 8
6.12.2 | Marshalling Kiosks for each 400kV Tie CB full-diameters, including: - 2 MUs and their test terminal blocks - 2 SCUs - Fiber Optic Organizer - AC/DC and other Auxiliary systems Combination of MUs/SCUs are possible based on the Digital substation Appendix | Lot | 4
6.12.3 | Marshalling Kiosks for each Power Transformer 400/132/11kV, including: - 5 MUs and their test terminal blocks (consider the accuracy required for ground CTs) - 1 SCUs (only inputs required) - Fiber Optic Organizer - AC/DC and other Auxiliary systems Combination of MUs/SCUs are possible based on the Digital substation Appendix | Lot | 2
6.12.4 | Marshalling Kiosks for each 400kV-50MVAR shunt reactor, including: - 3 MUs and their test terminal blocks (consider the accuracy required for ground CTs) - 1 SCUs (only inputs required) - Fiber Optic Organizer - AC/DC and other Auxiliary systems Combination of MUs/SCUs are possible based on the Digital substation Appendix | Lot | 2
6.12.5 | Marshalling Kiosks for each 132kV OHL with LPIT CT, including: - 1 Stand Alone MUs and their test terminal blocks - 1 MU as part of the LPIT and their test terminal blocks - 2 SCUs - Fiber Optic Organizer - AC/DC and other Auxiliary systems Combination of MUs/SCUs are possible based on the Digital substation Appendix | Lot | 2
6.12.6 | Marshalling Kiosks for each 132kV OH without LPIT CT, including: - 2 Stand Alone MUs and their test terminal blocks - 2 SCUs - Fiber Optic Organizer - AC/DC and other Auxiliary systems Combination of MUs/SCUs are possible based on the Digital substation Appendix | Lot | 2
6.12.7 | Marshalling Kiosks for each 132kV Transformer feeder, including: - 2 MUs and their test terminal blocks - 2 SCUs - Fiber Optic Organizer - AC/DC and other Auxiliary systems Combination of MUs/SCUs are possible based on the Digital substation Appendix | Lot | 2
6.12.8 | Marshalling Kiosks for each 132kV coupler or bus section (combining MKs might be possible based on distances), including: - 2 MUs and their test terminal blocks - 1 SCUs - Fiber Optic Organizer - AC/DC and other Auxiliary systems Combination of MUs/SCUs are possible based on the Digital substation Appendix | Lot | 4
TOTAL PRICE ITEM 6
7 | TELECOMMUNICATION & NCC/RCC
7.1 | New Telecommunication System for 400/132kV Substation. | Lot | 1
7.2 | New Tele protection Signaling Equipment for 400/132kV Substation. | Lot | 1
7.3 | New IP PABX and Telephone Equipment for 400/132kV Substation. | Lot | 1
7.4 | Incorporate new and modified substation equipment into the SCADA/EMS System at the NCC/RCC. | Lot | 1
7.5 | Modifications to NCC/RCC databases and applications | Lot | 1
7.6 | Update of the Geographic Map | Lot | 1
7.7 | Modifications to NCC/RCC operator displays | Lot | 1
7.8 | Modifications to NCC/RCC mimic board | Lot | 1
7.9 | Modification of Remote end Substation Telecommunication System | Lot | 1
TOTAL PRICE ITEM 7
8 | LV CABLES AND ACCESSORIES
8.1 | Auxiliary power and control cabling | Lot | 1
8.2 | Substation internal fibre optic cabling | Lot | 1
8.3 | Cabling installation hardware e.g. cable tray supports, cable trays, fixing hardware, glands, lugs, fire proof sealing of ducts/conduits/openings etc. | Lot | 1
TOTAL PRICE ITEM 8
9 | EARTHING & LIGHTNING PROTECTION
9.1 | Earthing system | Lot | 1
9.2 | Potable Earth leads | Set | 2
9.3 | Lightning protection system | Lot | 1
TOTAL PRICE ITEM 9
10 | 11KV CABLE SYSTEM
10.1 | 11kV cable system for connection between IBT and Earthing/auxiliary transformer | Lot | 2
10.2 | Cabling installation hardware e.g. cable trays etc. | Lot | 2
TOTAL PRICE ITEM 10
11 | SUPPORT STRUCTURES
11.1 | Steel supports for 400kV equipment including all accessories | Lot | 1
11.2 | Steel supports for 132kV equipment including all accessories | Lot | 1
11.3 | Gantries and other structures within substation | Lot | 1
11.4 | Structures for interconnecting 400kV and 132kV switchyards | Lot | 1
TOTAL PRICE ITEM 11
12 | CIVIL WORKS
12.1 | Hydrological and topographical site survey (based on substation layout dimension and dimension of allocated land) | Lot | 1
12.2 | Site clearance like removal of shrubs, bushes, vegetation, buildings, foundations as necessary | Lot | 1
12.3 | Earth works including excavation, backfilling and excavation in rock up to a depth of 2m | Lot | 1
12.4 | Soil Investigation | Lot | 1
12.5 | Temporary works | Lot | 1
12.6 | Grading and landscaping on completion | Lot | 1
12.7 | Surfacing with gravel | Lot | 1
12.8 | Switchyard internal Roads | Lot | 1
12.9 | Substation Drainage system | Lot | 1
12.10 | Sewage system | Lot | 1
12.11 | Water supply system including borehole | Lot | 1
12.12 | Substation land perimeter chain link fence including security for watch and ward during construction phase ( based on proposed substation layout) | m | approx. 1350
12.13 | Switchyard chain link fence | Lot | 1
12.14 | Substation gate | Lot | 1
12.15 | Cable trenching / ducts with cable trays for cable trenches | Lot | 1
12.16 | Substation road lighting | Lot | 1
12.17 | Substation compound lighting | Lot | 1
12.18 | Substation guard house & Telecom collocation room including building services e.g. Lighting, Small Power System, HVAC, Fire Detection, based on drawing and description
12.18.1 | Guard House Civil and Structural Works | Lot | 1
12.18.2 | Small power and electrical building services | Lot | 1
12.18.3 | HVAC and air conditioning | Lot | 1
12.18.4 | Internal lighting | Lot | 1
12.18.5 | Fire detection system | Lot | 1
12.18.6 | Drainage and Plumbing system | Lot | 1
12.18.7 | Access control system | Lot | 1
12.19 | Substation Control building including building services (e.g. Lighting, Small Power System, HVAC, Fire Detection), Eyewash facility and access control system.
12.19.1 | Control Building Civil and Structural Works | Lot | 1
12.19.2 | Small power and electrical building services | Lot | 1
12.19.3 | HVAC and air conditioning | Lot | 1
12.19.4 | Internal lighting | Lot | 1
12.19.5 | Fire detection system | Lot | 1
12.19.6 | Drainage and Plumbing system | Lot | 1
12.19.7 | Access control system | Lot | 1
12.20 | Covered Car parking for Control Building | Lot | 1
12.21 | Central Policing Infrastructure Unit Housing (CIPU) units including building services (e.g. Lighting, Small Power System, HVAC, Fire Detection)
12.21.1 | Central Policing Infrastructure Unit Housing (CIPU) units Civil and Structural Works | Lot | 4
12.21.2 | Small power and electrical building services | Lot | 4
12.21.3 | HVAC and air conditioning | Lot | 4
12.21.4 | Internal lighting | Lot | 4
12.21.5 | Fire detection system | Lot | 4
12.21.6 | Drainage and Plumbing system | Lot | 4
12.21.7 | Access control system | Lot | 4
12.21.8 | Chain link fence surrounding CIPU units | Lot | 1
12.22 | Warehouse including building services (e.g. Lighting, Small Power System, HVAC, Fire Detection) and also open storage area
12.22.1 | Warehouse Civil and Structural Works | Lot | 1
12.22.2 | Small power and electrical building services | Lot | 1
12.22.3 | HVAC and air conditioning | Lot | 1
12.22.4 | Internal lighting | Lot | 1
12.22.5 | Fire detection system | Lot | 1
12.22.6 | Drainage and Plumbing system | Lot | 1
12.22.7 | Access control system | Lot | 1
12.22.8 | Civil works for Open storage area including chain link fence | Lot | 1
12.22.9 | Overhead crane system including but not limited to supply, installation and commissioning with all associated associated accessories. | Lot | 1
12.23 | Diesel generator house based on dimension of generator along with generator house/building.
12.23.1 | Diesel generator units Civil and Structural Works | Lot | 1
12.23.2 | Small power and electrical building services | Lot | 1
12.22.3 | HVAC and air conditioning | Lot | 1
12.23.4 | Internal lighting | Lot | 1
12.23.5 | Fire detection system | Lot | 1
12.23.6 | Drainage and Plumbing system | Lot | 1
12.23.7 | Access control system | Lot | 1
12.24 | Foundation for 400kV equipment/support/gantries structures | Lot | 1
12.25 | Foundation for 132kV equipment/support/gantries structures | Lot | 1
12.26 | Foundation for Water tank, CCTV camera poles, covered car park and other equipment within the substation | Lot | 1
12.27 | Foundation for Structures for interconnecting 400kV and 132kV switchyards | Lot | 1
12.28 | Miscellaneous foundation to complete the requirements of work | Lot | 1
12.29 | IBT Plinth and oil containment tank | Set | 2
12.29.1 | IBT oil separation tank for two transformers complete | No. | 1
12.30 | Plinth and oil containment tank for busbar reactor | Set | 2
12.31 | Earthing/Auxiliary Transformer Plinth and oil containment tank. | Set. | 2
12.32 | Firewalls between two transformers and two reactors | Lot | 1
12.33 | Water system with automatic controls as detailed in clause 41.33.7.1.2 | Lot | 1
12.34 | Substation asphalt access/approach road from the Makindu substation to Mombasa road complete with drainage facilities and culverts as necessary. | km | Approx. 6
TOTAL PRICE ITEMS 12
13 | AUXILIARY SUPPLY
13.1 | Control building LVAC system based on drawings including two AC panels with bus sections with CB and detection of voltage. It will be provided connection to ET1, ET2 and generator with automatic changeover and interlocking. The LVAC panel should have meters with CL 0.2 for the incomers from Auxiliary/Earthing transformers | Lot | 1
13.2 | 110VDC System Control Building
13.2.1 | 110VDC Distribution board with auto changeover in main control building | Lot | 1
13.2.2 | 110VDC Chargers in main control building | Lot | 1
13.2.3 | 110VDC batteries in main control building | Lot | 1
13.3 | 48VDC System Control Building
13.3.1 | 48VDC Distribution board with auto changeover in main control building | Lot | 1
13.3.2 | 48VDC Chargers in main control building | Lot | 1
13.3.3 | 48VDC batteries in main control building | Lot | 1
13.4 | 415V Inverter system, minimum 4KVA including inverters, static switch, manual bypass switch & distribution panels | Lot | 1
13.5 | Earthing (Auxiliary) transformer 11/0.415kV, 500kVA - for whole substation | No. | 2
13.6 | Diesel Generator 250kVA including generator control and protection panel for whole substation | No. | 1
TOTAL PRICE ITEM 13
14 | TARIFF METERING
14.1 | Tariff metering panel for 400kV OHL feeders, complete with wiring, accessories etc. and including: | Lot | 2
14.1.1 | Main Meter | No. | 4
14.1.2 | Check Meter | No. | 4
14.2 | Tariff metering panel for 132kV OHL feeders complete with wiring, accessories etc. | Lot | 1
14.2.1 | Main Meter | No. | 2
14.2.2 | Check Meter | No. | 2
14.3 | Tariff metering panel for 132kV transformer incomer feeders complete with wiring, accessories etc. | Lot | 1
14.3.1 | Main Meter | No. | 2
14.3.2 | Check Meter | No. | 2
TOTAL PRICE ITEM 14
15 | FAULT/RECORDING MONITORING SYSTEM
15.1 | Fault Monitoring Panel including:
15.1.1 | Data Acquisition Units Signals inputs via IEC61850 SV and GOOSE | Lot | 1
15.1.2 | Master Station | No. | 1
15.1.3 | Local HMI | No. | 1
15.1.4 | Printer | No. | 1
TOTAL PRICE ITEM 15
16 | MISCELLANEOUS
16.1 | Padlocks / Keys (Access control system for Control building ) | Lot | 1
16.2 | Equipment labels, safety warning plates, road signage's, room name plates etc. | Lot | 1
16.3 | Protection and control panel labels, relay labels, LVAC/DC Panel labels & feeder names in switchyard at remote substations | Lot | 1
16.4 | VT/CT Marshalling Box | Lot | 1
16.5 | Gas Handling Trolley including accessories | Lot | 1
16.6 | Laptops as desribed in technical specification | No. | 10
16.7 | Mobile phones with usage charges of KES 5,000/- per month per phone | No. | 10
16.8 | CSR project | Lot | 1
16.9 | Tree growing Initiative | Lot | 1
16.10 | CPC 100 Multifunctional Primary Test System | No. | 1
16.11 | CMC 356 Protection system Test System, including RelaySimTest and IEC61850 licenses | No. | 1
16.12 | DANEO 400 Mergin Units tester and Network Analyzer | No. | 1
16.13 | StationScout Test System | No. | 1
16.14 | Portable Earth Leads | Set | 6
16.15 | CCTV system for 400kV & 132kV | Lot | 1
16.16 | All kinds of furnitures as detailed under Item 27.21 of Part-2 , Employers requirement. | Lot | 1
16.17 | Codes and standards as mentioned in the Employer requirements, section 7.1 | Lot | 2
16.18 | Document Management system active upon contract effectiveness until end of Defect liability period | lot | 1
TOTAL PRICE ITEM 16
17 | SITE TRANSPORT, SITE OFFICE AND PERMANENT LIVING ACCOMMODATION, STAFF TRAINING, INTERSHIP COSTS
17.1 | Transport Services and Vehicles
17.1.1 | Transport Services - Vehicle Type 1 | No. | 6
17.1.2 | Vehicle Type 2 | No. | 1
17.2 | Site Office fully furnished as specified in the Employer's Requirements and with fully furnished kitchenettes, Storage Facilities. | Lot | 1
17.3 | Site and staff training as per employer's requirement | Lot | 1
17.3.1 | Training on the Site:
17.3.1.1 | OMICRON CMC 356 Three Phase Secondary Injection Kit complete with 2CMGPS and Two RelaySim Test Software and IEC 61850 license. | Lot | 1
17.3.1.2 | OMICRON DANEO 400 Hybrid network analyzer for testing Mergin Units and communication network | Lot | 1
17.3.1.3 | OMICRON Station Scout, Substation Automation test set | Lot | 1
17.3.1.4 | CPC 100 Multifunctional Primary Test System | Lot | 1
17.3.1.5 | 11kV cable training | Lot | 1
17.3.1.6 | Solar water heating system | Lot | 1
17.3.1.7 | Site Operation and Maintenance Training (20 Engineers for 2 weeks) | Lot | 1
17.3.2 | Training at Contractor Home Office as per Employers Requirements
17.3.2.1 | Protection and Control for Electrical Power Systems (8 Engineers for 2 weeks): | Lot | 1
17.3.2.2 | Power System Analysis (8 Engineers for 2 weeks) | Lot | 1
17.3.2.3 | Substation Electrical Design (8 Engineers for 2 weeks) including softwares supply | Lot | 1
17.3.2.4 | Communication & SCADA– Application & Design (8 Engineers for 2 weeks) | Lot | 1
17.3.2.5 | Civil Engineering Design (8 Engineers for 2 weeks) | Lot | 1
17.3.2.6 | Training on Digital Fault Recorder, Fault Locator and Phasor Measurement unit (PMU)(8 Engineers for 2 weeks) | Lot | 1
17.3.2.7 | Training on Digital substation and Cyber security 2 batches of 8 Engineers per batch for 4 weeks. | Lot | 1
17.3.2.8 | Proposed Internship program for engineering students (shall be approved by KETRACO)-10 students | Lot | 1
17.3.2.9 | Knowledge and skill transfer to local engineers | Lot | 1
17.3.3 | Softwares as decribed in Section 2, Chapter 1 of the Employer's Requirements
17.3.3.1 | AutoCAD for windows - Premium plan subcription including training | No. | 2
17.3.3.2 | AutoCAD for windows with AutoCAD Electrical toolset - premium plan subscritpion including training | No. | 1
17.3.3.3 | PSSE (maintenance and support) including training | No. | 2
17.3.3.4 | PLS CADD (subscription) including training | No. | 3
17.3.5.5 | PLS Tower (subscription) including training | No. | 5
TOTAL PRICE ITEM 17
18 | DESIGN REVIEW MEETING
18.1 | Design review meeting at the Contractor’s home country’s design office as per Employers Requirements | Lot | 1
TOTAL PRICE ITEM 18
19 | MANDATORY SPARE PARTS
19.1 | 400kV Circuit breaker (1 Pole operated -3 phase) Complete with mechanism box , Central Control Panel, complete with operating platform. All accessories will be included to make testing and commissioning completed | No. | 1
19.2 | 132kV Circuit breaker (3 pole/gang operated, 3 phase) Complete with mechanism/central box (with current rating same as bus coupler ). All accessories will be included to make testing and commissioning completed, complete with operating platform. | No. | 1
19.3 | 400 kV Post type current transformer for Protection & Measuring (1-phase) as per TDS All accessories will be included to make testing and commissioning completed. | No. | 3
19.4 | 132 kV Post type current transformer for Protection & Measuring (1-phase) for the OHL feeder as per TDS All accessories will be included to make testing and commissioning completed. | No. | 3
19.5 | 400 kV Post type Capacitive Voltage Transformer for Protection & Measuring (1-phase) as per TDS All accessories will be included to make testing and commissioning completed. | No. | 3
19.6 | 132 kV Post type Capacitive Voltage Transformer for Protection & Measuring (1-phase) as per TDS All accessories will be included to make testing and commissioning completed. Phase summation galvanized junction box will be provided | No. | 3
19.7 | Low Power Instrument Transformer (LPIT), or Optical CT | No. | 1
19.8 | 400kV Line distance Protection relay as per TDS | No. | 1
19.9 | 400kV Line differential Protection relay as per TDS | No. | 1
19.10 | Transformer differential Protection relay as per TDS | No. | 1
19.11 | 400kV bus bar protection relay as per TDS | No. | 1
19.12 | 132kV bus bar protection relay as per TDS | No. | 1
19.13 | Transformer HVC protection relay as per TDS | No. | 1
19.14 | Bay Control Unit used in 400kV substation as per TDS | No. | 1
19.15 | Bay Control Unit used in 132kV substation as per TDS | No. | 1
19.16 | Phasor measurement unit,PMU relay | No. | 1
19.17 | Common Bay control Unit, as per TDS | No. | 1
19.18 | Managed Ethernet switches | No. | 2
19.19 | Power transformer Gaskets | Lot | 1
19.20 | Transformer back up protection relay-HV | No. | 1
19.21 | Transformer back up protection relay-LV | No. | 1
19.22 | Industrial Eth switch 24 ports, PTP capable | No. | 6
19.23 | Industrial Eth switch 8/10 ports, PTP capable | No. | 2
19.24 | Industrial Redbox - 8 ports, PTP and PRP capable | No. | 2
19.25 | Merging Unit IEC61850/IEC61869-9 | No. | 8
19.26 | Switch Controller Unit SCU | No. | 4
19.27 | Grand Master Clock PTP, PRP capable | No. | 1
19.28 | GPS antenna | No. | 1
19.29 | Firewall: SSL/TSL/SSH/NAT, 6 ports, throughput 1.4 Gbps | No. | 1
19.30 | Gateway Computer | No. | 1
19.31 | Station SCADA Computer | No. | 1
19.32 | one of each telecommunication cards used complete with the terminations, set of long range SFP modules | Lot | 1
19.33 | 2 x 48 core ODF complete with pigtail | Lot | 1
TOTAL PRICE ITEM 19
20 | Factory Acceptance Tests(FAT):
20.1 | Power transformers | LS | 1
20.2 | Earthing/Auxiliary Transformers | LS | 1
20.3 | Shunt reactors | LS | 1
20.4 | Circuit Breakers | LS | 1
20.5 | Disconnector and Earthing switches | LS | 1
20.6 | Instrument Transformers(CT & CVT) | LS | 1
20.7 | Low power Instrument Transformers (LPIT) | LS | 1
20.8 | Surge arrestors | LS | 1
20.9 | Post & Longrod insulators | LS | 1
20.10 | Busbar, Clamps & fittings | LS | 1
20.11 | Equipment steel structures and gantries | LS | 1
20.12 | AC/DC panels, battery chargers | LS | 1
20.13 | Protection, control, Metering, SCU, MU and SCADA system including digital substation | LS | 1
20.14 | Telecommunication equipment | LS | 1
20.15 | Fault monitoring systems/Fault recorder | LS | 1
TOTAL PRICE ITEM 20
TOTAL PRICE SCHEDULE 1 MAKINDU SUBSTATION
Name of the Bidder
Country of origin Declaration Form
Item | Description |  |  |  | Country

## Schedule 2_SS
400/132kV MAKINDU SUBSTATION
Schedules of Rates and Prices
Schedule No. 2
Plant and Mandatory Spare Parts Supplied from within the Employer's Country
Item | Description | Unit | Qty | Unit Price |  | Total Price
|  |  |  | Foreign Currency | Local Currency (KSh) = KENYAN SHILLINGS | Foreign Currency | Local Currency (KSh) = KENYAN SHILLINGS
|  |  | (1) | (2) | (3) | (4)=(1)* (2) | (5)=(1)*(3)
Bidders shall enter a code representing the country of origin of all imported plant and equipment.
Specify currency create and use as many columns for unit price and total price as there are currencies
1 | 400kV PRIMARY PLANT
1.1 | Circuit breaker (1 Pole operated -3 phase) Complete with mechanism box , Central Control Panel, complete with operating platform. All accessories will be included to make testing and commissioning completed . | No. | 12
1.2 | Disconnector, motorized (1 Pole operated-3-phase) with earth mat, Complete with Central Control Panel. All accessories will be included to make testing and commissioning completed. | No. | 24
1.3 | Disconnector, motorized (1 Pole operated-3 phase) complete with one integral motorized earth switch and earth mat, Complete with Central Control Panel. All accessories will be included to make testing and commissioning completed. | No. | 8
1.4 | Surge arrester (1-phase) including surge counter with earth leakage meter connecting to earth grid. All accessories will be included to make testing and commissioning completed. | No. | 24
1.5 | Post insulator -for main busbar, All accessories will be included to make testing and commissioning completed | Lot | 1
1.6 | Post insulator - for bay busbar, All accessories will be included to make testing and commissioning completed | Lot | 1
1.7 | Post insulator - Under-hung All accessories will be included to make testing and commissioning completed | Lot | 1
1.8 | Strain (Longrod)insulator - with turnbuckle All accessories will be included to make testing and commissioning completed | Lot | 1
1.9 | Strain(Longrod) insulator - without turnbuckle All accessories will be included to make testing and commissioning completed. | Lot | 1
1.10 | Post type current transformer for Protection & Measuring (3 Core,1-phase) for lines. All accessories will be included to make testing and commissioning completed. Phase summation galvanized junction box will be provided. | No. | 24
1.11 | Post type current transformer for Protection & Measuring (3 Core,1-phase).for transformers All accessories will be included to make testing and commissioning completed. Phase summation galvanized junction box will be provided. | No. | 12
1.12 | Post type current transformer -High Accuracy Tariff metering (2 Core, 1-phase) All accessories will be included to make testing and commissioning completed. Phase summation galvanized junction box will be provided. | No. | 12
1.13 | Capacitive voltage transformer - (Protection & Measuring, 1-phase) Supply will be based on TDS and description. All accessories will be included to make testing and commissioning completed . Phase summation galvanized junction box will be provided | No. | 20
1.14 | Capacitive Voltage transformer (1-phase) (High Accuracy Metering) Supply will be based on TDS and description. All accessories will be included to make testing and commissioning completed. Phase summation galvanized junction box will be provided. | No. | 12
1.15 | Conductor - Tubular Supply will be based on TDS and description. All accessories will be included to make testing and commissioning completed. | Lot | 1
1.16 | Conductor - Stranded Supply will be based on TDS and description. All accessories will be included to make testing and commissioning completed. | Lot | 1
1.17 | Connectors - Tube ; All accessories will be included to make testing and commissioning completed | Lot | 1
1.18 | Connectors - for Stranded flashover, down-droppers, equipment connect.etc. All accessories will be included to make testing and commissioning completed | Lot | 1
TOTAL PRICE ITEM 1
2 | 132kV PRIMARY PLANT
2.1 | Circuit breaker (3 pole/gang operated, 3 phase) Complete with mechanism/central box ( IBT1 & 2, Bus sections ). All accessories will be included to make testing and commissioning completed, complete with operating platform. | No. | 4
2.2 | Circuit breaker (3 pole/gang operated, 3 phase) Complete with mechanism/central box (for bus coupler ). All accessories will be included to make testing and commissioning completed, complete with operating platform. | No. | 2
2.3 | Circuit breaker (1 pole operated-3 phases) for OHL Complete with mechanism box/Central Control Panel. All accessories will be included to make testing and commissioning completed complete with operating platform | No. | 2
2.4 | Disconnector, motorized (3-phase) with earth math connecting to earth grid(busbar DS for IBT1 & IBT 2 and OHL). All accessories will be included to make testing and commissioning completed | No. | 8
2.5 | Disconnector, motorized (3-phase) with earth math connecting to earth grid(for bus couplers). All accessories will be included to make testing and commissioning completed | No. | 4
2.6 | Disconnector, motorized (3-phase) complete with one integral earth switch(for IBT 1& IBT 2 and OHLs) All accessories will be included to make testing and commissioning completed. Earth mat will be provided connected to earth grid. | No. | 4
2.7 | Disconnector, motorized (3-phase) complete with two integral motorized earth switches(for bus sections) All accessories will be included to make testing and commissioning completed. Earth mat will be provided connected to earth grid. | No | 4
2.8 | Surge arrester (1-phase) including surge counter with earth leakage meter connecting to earth greed All accessories will be included to make testing and commissioning completed. | No. | 12
2.9 | Post insulator - for the main busbar, All accessories will be included to make testing and commissioning completed | Lot | 1
2.10 | Post insulator - for the bay busbar support, All accessories will be included to make testing and commissioning completed | Lot | 1
2.11 | Post insulator - Under-hung All accessories will be included to make testing and commissioning completed | Lot | 1
2.12 | Strain (Longrod) insulator - with turnbuckle All accessories will be included to make testing and commissioning completed | Lot | 1
2.13 | Strain (Longrod) insulator - without turnbuckle All accessories will be included to make testing and commissioning completed | Lot | 1
2.14 | 132kV Post type current transformer for IBT Protection & Metering. (1-phase, 4 cores) with galvanized phase summation junction box. All accessories will be included to make testing and commissioning completed | No. | 6
2.15 | 132kV Post type current transformer for OHL Protection & Metering. (1-phase, 4 cores) with galvanized phase summation junction box. All accessories will be included to make testing and commissioning completed | No. | 6
2.16 | 132kV Post type current transformer, for Bus section and bus coupler (1-phase, 2 cores) with galvanized phase summation junction box. All accessories will be included to make testing and commissioning completed | No. | 24
2.17 | 132kV Capacitive voltage Transformer of Protection & Measuring (1-phase, three cores) for 132kV busbar. All accessories will be included to make testing and commissioning completed. | No | 4
2.18 | 132kV Capacitive voltage transformer - (1-phase, High Accuracy Metering) for protection and metering with galvanized phase summation box. All accessories will be included to make testing and commissioning completed | No. | 12
2.19 | Conductor - Tube - 132kV Bus bar 1&2 - min. 100mm dia All accessories will be included to make testing and commissioning completed | Lot | 1
2.20 | Conductor - Stranded (overfly/down drop and equipment connection) All accessories will be included to make testing and commissioning completed | Lot | 1
2.21 | Connectors - Tube min. 100mm dia (132kv Bus bar) All accessories will be included to make testing and commissioning completed | Lot | 1
2.22 | Connectors - Stranded conductor All accessories will be included to make testing and commissioning completed | Lot | 1
2.23 | Low Power Instrument Transformer (LPIT),or Optical CT with all accessories necessary for complete testing and commissioning | No | 3
TOTAL PRICE ITEM 2
3 | Power Transformer and Busbar Reactor
3.1 | INTERBUS TRANSFORMER (IBT - Three windings)
3.1.1 | Three phase units with three windings 400/132/11kV, 75/90 MVA (ONAN/ONAF) including HV/LV/TV/Neutral CT's & Bushing CTs | No. | 2
3.1.2 | Fire Protection system with Nitrogen Injection & Oil Evacuation System, explosion proof, based on description in Tender document (all accessories including trolley fire extinguisher, sand box , shovels and buckets(at least 2 sets)shall be included to make testing and commissioning completed) | No. | 2
3.1.3 | Power transformer online monitoring system based on description in Tender document (all accessories will be included to make testing and commissioning completed). | No. | 2
3.1.4 | Parallel transformer online operation system using IEC 61850 GOOSE communication and interconnecting in master -follower mode (based on description on description in Tender document ), (all accessories will be included to make testing and commissioning completed). | Lot | 1
3.1.5 | Surge arrester (1-phase), installed in the Power TX11kV cable box | No. | 6
3.2 | Busbar Shunt Reactor
3.2.1 | Three phase units with three windings 400kV, 50MVAR Reactor including HV and Neutral CT's & Bushing CTs | No. | 2
TOTAL PRICE ITEM 3
4 | 400kV PROTECTION SYSTEMS
4.1 | 400kV OHL Protection System (4 sets)
4.1.1 | Main 1 21L Protection (different vendor from Main 2) | No. | 4
4.1.2 | Main 2 87L Protection (different vendor from Main 1) | No. | 4
4.1.3 | Auto-Reclose Protection function (included within Main 1 and Main2) | No. | 4
4.1.4 | Panels including all accessories, e.g. AC/DC system, wiring etc. to make the system complete | Panels (No) | 4
4.1.6 | Point on Wave controller | No. | 8
4.1.5 | Phasor Measurement Unit (PMU) including PDC, and accessories required to integrate in KETRACO's SDH network | Lot | 1
4.2 | 400kV HV Transformer Protection System including (2 sets):
4.2.1 | Main 87T+87N Protection | No. | 2
4.2.2 | Backup 50/51(N) Protection and HV Neutral 51N Stand-by Earth-Fault Protection | No. | 2
4.2.3 | 87HVC1 Connection Protection (different vendor from Main 87HVC2) | No. | 2
4.2.4 | 87HVC2 Connection Protection (different vendor from Main 87HVC1) | No. | 2
4.2.5 | Panels including all accessories, e.g. AC/DC system, wiring etc. to make the system complete | Panels (No) | 4
4.2.6 | Point on Wave controller | No. | 2
4.3 | 400kV HV Busbar Shunt Reactor including (2 sets):
4.3.1 | Main 87R+87NR Protection | No. | 2
4.3.2 | Backup 50/51(N) Protection | No. | 2
4.3.3 | 87HVC1 Connection Protection (different vendor from Main 87HVC2) | No. | 2
4.3.4 | 87HVC2 Connection Protection (different vendor from Main 87HVC1) | No. | 2
4.3.5 | Panels including all accessories, e.g. AC/DC system, wiring etc. to make the system complete | Panels (No) | 2
4.3.6 | Point on Wave controller | No. | 2
4.4 | 400kV Bus bar Protection System 400kV Bus bar Protection (BUS BAR 1 &2 ). All accessories will be included to make testing and commissioning completed. | Lot | 2
4.4.1 | The 50BF function shall be included for CBS as per SLDs | No | 8
4.5 | Modification works in remote substation Rabai or Mariakani & Isinya Substation. Including relay setting & relay configuration etc. | Lot | 1
4.6 | Miscellaneous modification works as necessary to make the complete 400kV protection system functional | Lot | 1
4.7 | Update the remote substations drawings (Rabai/Mariakani and Isinya) | Lot | 1
TOTAL PRICE ITEM 4
5 | 132kV PROTECTION SYSTEMS
5.1 | 132kV OHL Protection System including: | Lot | 2
5.1.1 | Main 1 21L Protection (different vendor from Main 2) | No. | 2
5.1.2 | Main 2 87L Protection (different vendor from Main 1) | No. | 2
5.1.3 | Auto-Reclose Protection function (included within Main 1 and Main2) | No. | 2
5.1.4 | Panels including all accessories, e.g. AC/DC system, wiring etc. to make the system complete | Panels (No) | 2
5.1.5 | Modification works at the remote end substations from Makindu substation including relay setting calculations & relay configuration & testing. | lot | 1
5.2 | 132kV LV Transformer Protection System including: | Lot | 2
5.2.1 | Backup 50/51(N),67/67N Protection, LV NEUTRAL, 51N, LV REF, LVSBEF | No. | 2
5.2.2 | Earthing Transformer 11kV side-87N/TV, 11kV side standby earth fault protection 51NTV, 50/51, TV REF and BCU | No. | 2
5.2.3 | The AVR Panel including all accessories including AVR, AVR relay, wiring etc. to make the system completes. (one panel for both) | Panels (No) | 2
5.2.4 | Panels including all accessories, e.g. AC/DC system, wiring etc. to make the system complete | Panels (No) | 2
5.3 | 132kV complete Bus bar Protection System - OHL Bus bar protections - TR bus bar protections - Bus coupler Bus bar protection - Bus section Bus bar protection - Bus bar panels | Lot | 1
5.4 | 132kV Protection - Bus coupler protection (integrated with BCU) - Bus section protection (integrated with BCU) - Bus coupler & Bus section shared panel | Lot | 2
5.5 | Miscellaneous modification works as necessary to make the complete 132kV protection system functional | Lot | 1
TOTAL PRICE ITEM 5
6 | 400/132kV SUBSTATION AUTOMATION SYSTEM
6.1 | 400/132kV Bay Control Units and panels: | Lot | 2
6.1.1 | Bay Control Units (BCU) 400kV (full diameters) - One BCU per CB. include 25 and VSL function - BCU for CB-Bus-OHL - BCU for CB-TIE include 50BF function - BCU for CB-Bus-Tx | Lot | 2
6.1.2 | Bay Control Units (BCU) 400kV (full diameters) - One BCU per CB. include 25 and VSL function - BCU for CB-Bus-OHL - BCU for CB-TIE include 50BF function - BCU for CB-Bus-Reactor | Lot | 2
6.1.3 | Bay Control Units (BCU) 132kV - One BCU per CB. include 25 and VSL function - BCU for OHL - BCU for Coupler (C&P combined ) - BCU for Bus-Section (C&P combined) - BCU for each Transformer feeder | Lot | 1
6.1.4 | Bay Control Panels - 400kV one panel per diameter - 132kV C&P combined in the same panel | Lot | 1
6.1.5 | Auxiliary and Common Services Bay Control Units BCUs, one per each Earthing Transformer 11/0.415kV, including 415V side-51N protection. Including one combined panel for both | Lot | 1
6.2 | 400/132kV Local Area Network: | Lot | 2
6.2.1 | PRP Process Bus Network composed of both LAN-A and LAN-B, 1000BaseFX, industrial Eth switches, PTP capable (technical requirements in Appendix), Physically independent thus: - PRP LAN A & LAN B, 400kV Diameter 1 - PRP LAN A & LAN B, 400kV Diameter 2 - PRP LAN A & LAN B, 400kV Diameter 3 - PRP LAN A & LAN B, 400kV Diameter 4 - PRP LAN A & LAN B, 132kV for two OHL bays - PRP LAN A & LAN B, 132kV for two Transformer bays - PRP LAN A & LAN B, 132kV for two couplers and two bus section bays Switches to be installed in the control cabinets of the corresponding bay | Lot | 1
6.2.2 | PRP Station Bus Network composed of both LAN-A and LAN-B, 100BaseFX, industrial Eth switches, PTP capable (technical requirements in Appendix) | Lot | 1
6.2.3 | PRP Process Bus Inter-bay Network composed of both LAN-A and LAN-B, 1000BaseFX, industrial Eth switches, PTP capable (technical requirements in Appendix), Physically independent thus | Lot | 1
6.2.4 | PRP Redboxes, 100BaseFX, PTP capable (technical requirements in Appendix), minimum 8 ports | Lot | 4
6.2.5 | RSTP DMZ Network, 100BaseTx, PTP capable (technical requirements in Appendix) | Lot | 1
6.2.6 | Outdoor armored Fiber optics and Fiber Optic Organizer for connections from the Marshaling Kiosks to the control room | Lot | 1
6.2.7 | Armed Fiber optics, patch cords FO, Patch cords Eth and other wiring necessary for the Network | Lot | 1
6.3 | Firewall: SSL/TSL/SSH/NAT, 6 ports, throughput 1.4 Gbps (technical requirements in Appendix) | Lot | 1
6.4 | Cybersecurity Intrution Detection and Functional Monitoring System | Lot | 2
6.5 | Human Machine Interface (OWS) | Lot | 2
6.6 | Engineering Workstation (EWS) | No. | 2
6.7 | SCADA servers | No. | 2
6.8 | Gateways | No. | 2
6.9 | Time synchronization system including clocks, antennas and accessories (see technical requirements in Digital substation Appendix) | No. | 2
6.10 | Laser Jet printer (A3 & A4) | No. | 1
6.11 | General Purpose Printer | No. | 1
6.12 | 400/132kV Digital interfaces: | Lot | 2
6.12.1 | Marshalling Kiosks for each 400kV Bus-side CB, including: - 3 MUs and their test terminal blocks - 2 SCUs - Fiber Optic Organizer - AC/DC and other Auxiliary systems Combination of MUs/SCUs are possible based on the Digital substation Appendix | Lot | 8
6.12.2 | Marshalling Kiosks for each 400kV Tie CB full-diameters, including: - 2 MUs and their test terminal blocks - 2 SCUs - Fiber Optic Organizer - AC/DC and other Auxiliary systems Combination of MUs/SCUs are possible based on the Digital substation Appendix | Lot | 4
6.12.3 | Marshalling Kiosks for each Power Transformer 400/132/11kV, including: - 5 MUs and their test terminal blocks (consider the accuracy required for ground CTs) - 1 SCUs (only inputs required) - Fiber Optic Organizer - AC/DC and other Auxiliary systems Combination of MUs/SCUs are possible based on the Digital substation Appendix | Lot | 2
6.12.4 | Marshalling Kiosks for each 400kV-50MVAR shunt reactor, including: - 3 MUs and their test terminal blocks (consider the accuracy required for ground CTs) - 1 SCUs (only inputs required) - Fiber Optic Organizer - AC/DC and other Auxiliary systems Combination of MUs/SCUs are possible based on the Digital substation Appendix | Lot | 2
6.12.5 | Marshalling Kiosks for each 132kV OHL with LPIT CT, including: - 1 Stand Alone MUs and their test terminal blocks - 1 MU as part of the LPIT and their test terminal blocks - 2 SCUs - Fiber Optic Organizer - AC/DC and other Auxiliary systems Combination of MUs/SCUs are possible based on the Digital substation Appendix | Lot | 2
6.12.6 | Marshalling Kiosks for each 132kV OH without LPIT CT, including: - 2 Stand Alone MUs and their test terminal blocks - 2 SCUs - Fiber Optic Organizer - AC/DC and other Auxiliary systems Combination of MUs/SCUs are possible based on the Digital substation Appendix | Lot | 2
6.12.7 | Marshalling Kiosks for each 132kV Transformer feeder, including: - 2 MUs and their test terminal blocks - 2 SCUs - Fiber Optic Organizer - AC/DC and other Auxiliary systems Combination of MUs/SCUs are possible based on the Digital substation Appendix | Lot | 2
6.12.8 | Marshalling Kiosks for each 132kV coupler or bus section (combining MKs might be possible based on distances), including: - 2 MUs and their test terminal blocks - 1 SCUs - Fiber Optic Organizer - AC/DC and other Auxiliary systems Combination of MUs/SCUs are possible based on the Digital substation Appendix | Lot | 4
TOTAL PRICE ITEM 6
7 | TELECOMMUNICATION & NCC/RCC
7.1 | New Telecommunication System for 400/132kV Substation. | Lot | 1
7.2 | New Tele protection Signaling Equipment for 400/132kV Substation. | Lot | 1
7.3 | New IP PABX and Telephone Equipment for 400/132kV Substation. | Lot | 1
7.4 | Incorporate new and modified substation equipment into the SCADA/EMS System at the NCC/RCC. | Lot | 1
7.5 | Modifications to NCC/RCC databases and applications | Lot | 1
7.6 | Update of the Geographic Map | Lot | 1
7.7 | Modifications to NCC/RCC operator displays | Lot | 1
7.8 | Modifications to NCC/RCC mimic board | Lot | 1
7.9 | Modification of Remote end Substation Telecommunication System | Lot | 1
TOTAL PRICE ITEM 7
8 | LV CABLES AND ACCESSORIES
8.1 | Auxiliary power and control cabling | Lot | 1
8.2 | Substation internal fibre optic cabling | Lot | 1
8.3 | Cabling installation hardware e.g. cable tray supports, cable trays, fixing hardware, glands, lugs, fire proof sealing of ducts/conduits/ openings etc. | Lot | 1
TOTAL PRICE ITEM 8
9 | EARTHING & LIGHTNING PROTECTION
9.1 | Earthing system | Lot | 1
9.2 | Potable Earth leads | Set | 2
9.3 | Lightning protection system | Lot | 1
TOTAL PRICE ITEM 9
10 | 11KV CABLE SYSTEM
10.1 | 11kV cable system for connection between IBT and Earthing/auxiliary transformer | Lot | 2
10.2 | Cabling installation hardware e.g. cable trays etc. | Lot | 2
TOTAL PRICE ITEM 10
11 | SUPPORT STRUCTURES
11.1 | Steel supports for 400kV equipment including all accessories | Lot | 1
11.2 | Steel supports for 132kV equipment including all accessories | Lot | 1
11.3 | Gantries and other structures within substation | Lot | 1
11.4 | Structures for interconnecting 400kV and 132kV switchyards | Lot | 1
TOTAL PRICE ITEM 11
12 | CIVIL WORKS
12.1 | Hydrological and topographical site survey (based on substation layout dimension and dimension of allocated land) | Lot | 1
12.2 | Site clearance like removal of shrubs, bushes, vegetation, buildings, foundations as necessary | Lot | 1
12.3 | Earth works including excavation, backfilling and excavation in rock up to a depth of 2m | Lot | 1
12.4 | Soil Investigation | Lot | 1
12.5 | Temporary works | Lot | 1
12.6 | Grading and landscaping on completion | Lot | 1
12.7 | Surfacing with gravel | Lot | 1
12.8 | Switchyard internal Roads | Lot | 1
12.9 | Substation Drainage system | Lot | 1
12.10 | Sewage system | Lot | 1
12.11 | Water supply system including borehole | Lot | 1
12.12 | Substation land perimeter chain link fence including security for watch and ward during construction phase ( based on proposed substation layout) | m | approx. 1350
12.13 | Switchyard chain link fence | Lot | 1
12.14 | Substation gate | Lot | 1
12.15 | Cable trenching / ducts with cable trays for cable trenches | Lot | 1
12.16 | Substation road lighting | Lot | 1
12.17 | Substation compound lighting | Lot | 1
12.18 | Substation guard house & Telecom collocation room including building services e.g. Lighting, Small Power System, HVAC, Fire Detection, based on drawing and description
12.18.1 | Guard House Civil and Structural Works | Lot | 1
12.18.2 | Small power and electrical building services | Lot | 1
12.18.3 | HVAC and air conditioning | Lot | 1
12.18.4 | Internal lighting | Lot | 1
12.18.5 | Fire detection system | Lot | 1
12.18.6 | Drainage and Plumbing system | Lot | 1
12.18.7 | Access control system | Lot | 1
12.19 | Substation Control building including building services (e.g. Lighting, Small Power System, HVAC, Fire Detection), Eyewash facility and access control system.
12.19.1 | Control Building Civil and Structural Works | Lot | 1
12.19.2 | Small power and electrical building services | Lot | 1
12.19.3 | HVAC and air conditioning | Lot | 1
12.19.4 | Internal lighting | Lot | 1
12.19.5 | Fire detection system | Lot | 1
12.19.6 | Drainage and Plumbing system | Lot | 1
12.19.7 | Access control system | Lot | 1
12.20 | Covered Car parking for Control Building | Lot | 1
12.21 | Central Policing Infrastructure Unit Housing (CIPU) units including building services (e.g. Lighting, Small Power System, HVAC, Fire Detection)
12.21.1 | Central Policing Infrastructure Unit Housing (CIPU) units Civil and Structural Works | Lot | 4
12.21.2 | Small power and electrical building services | Lot | 4
12.21.3 | HVAC and air conditioning | Lot | 4
12.21.4 | Internal lighting | Lot | 4
12.21.5 | Fire detection system | Lot | 4
12.21.6 | Drainage and Plumbing system | Lot | 4
12.21.7 | Access control system | Lot | 4
12.21.8 | Chain link fence surrounding CIPU units | Lot | 1
12.22 | Warehouse including building services (e.g. Lighting, Small Power System, HVAC, Fire Detection) and also open storage area
12.22.1 | Warehouse Civil and Structural Works | Lot | 1
12.22.2 | Small power and electrical building services | Lot | 1
12.22.3 | HVAC and air conditioning | Lot | 1
12.22.4 | Internal lighting | Lot | 1
12.22.5 | Fire detection system | Lot | 1
12.22.6 | Drainage and Plumbing system | Lot | 1
12.22.7 | Access control system | Lot | 1
12.22.8 | Civil works for Open storage area including chain link fence | Lot | 1
12.22.9 | Overhead crane system including but not limited to supply, installation and commissioning with all associated associated accessories. | Lot | 1
12.23 | Diesel generator house based on dimension of generator along with generator house/building.
12.23.1 | Diesel generator units Civil and Structural Works | Lot | 1
12.23.2 | Small power and electrical building services | Lot | 1
12.22.3 | HVAC and air conditioning | Lot | 1
12.23.4 | Internal lighting | Lot | 1
12.23.5 | Fire detection system | Lot | 1
12.23.6 | Drainage and Plumbing system | Lot | 1
12.23.7 | Access control system | Lot | 1
12.24 | Foundation for 400kV equipment/support/gantries structures | Lot | 1
12.25 | Foundation for 132kV equipment/support/gantries structures | Lot | 1
12.26 | Foundation for Water tank, CCTV camera poles, covered car park and other equipment within the substation | Lot | 1
12.27 | Foundation for Structures for interconnecting 400kV and 132kV switchyards | Lot | 1
12.28 | Miscellaneous foundation to complete the requirements of work | Lot | 1
12.29 | IBT Plinth and oil containment tank | Set | 2
12.29.1 | IBT oil separation tank for two transformers complete | No. | 1
12.30 | Plinth and oil containment tank for busbar reactor | Set | 2
12.31 | Earthing/Auxiliary Transformer Plinth and oil containment tank. | Set. | 2
12.32 | Firewalls between two transformers and two reactors | Lot | 1
12.33 | Water system with automatic controls as detailed in clause 41.33.7.1.2 | Lot | 1
12.34 | Substation asphalt access/approach road from the Makindu substation to Mombasa road complete with drainage facilities and culverts as necessary. | km | Approx. 6
TOTAL PRICE ITEMS 12
13 | AUXILIARY SUPPLY
13.1 | Control building LVAC system based on drawings including two AC panels with bus sections with CB and detection of voltage. It will be provided connection to ET1, ET2 and generator with automatic changeover and interlocking. The LVAC panel should have meters with CL 0.2 for the incomers from Auxiliary/Earthing transformers | Lot | 1
13.2 | 110VDC System Control Building
13.2.1 | 110VDC Distribution board with auto changeover in main control building | Lot | 1
13.2.2 | 110VDC Chargers in main control building | Lot | 1
13.2.3 | 110VDC batteries in main control building | Lot | 1
13.3 | 48VDC System Control Building
13.3.1 | 48VDC Distribution board with auto changeover in main control building | Lot | 1
13.3.2 | 48VDC Chargers in main control building | Lot | 1
13.3.3 | 48VDC batteries in main control building | Lot | 1
13.4 | 415V Inverter system, minimum 4KVA including inverters, static switch, manual bypass switch & distribution panels | Lot | 1
13.5 | Earthing (Auxiliary) transformer 11/0.415kV, 500kVA - for whole substation | No. | 2
13.6 | Diesel Generator 250kVA including generator control and protection panel for whole substation | No. | 1
TOTAL PRICE ITEM 13
14 | TARIFF METERING
14.1 | Tariff metering panel for 400kV OHL feeders, complete with wiring, accessories etc. and including: | Lot | 2
14.1.1 | Main Meter | No. | 4
14.1.2 | Check Meter | No. | 4
14.2 | Tariff metering panel for 132kV OHL feeders complete with wiring, accessories etc. | Lot | 1
14.2.1 | Main Meter | No. | 2
14.2.2 | Check Meter | No. | 2
14.3 | Tariff metering panel for 132kV transformer incomer feeders complete with wiring, accessories etc. | Lot | 1
14.3.1 | Main Meter | No. | 2
14.3.2 | Check Meter | No. | 2
TOTAL PRICE ITEM 14
15 | FAULT/RECORDING MONITORING SYSTEM
15.1 | Fault Monitoring Panel including:
15.1.1 | Data Acquisition Units Signals inputs via IEC61850 SV and GOOSE | Lot | 1
15.1.2 | Master Station | No. | 1
15.1.3 | Local HMI | No. | 1
15.1.4 | Printer | No. | 1
TOTAL PRICE ITEM 15
16 | MISCELLANEOUS
16.1 | Padlocks / Keys (Access control system for Control building ) | Lot | 1
16.2 | Equipment labels, safety warning plates, road signage's, room name plates etc. | Lot | 1
16.3 | Protection and control panel labels, relay labels, LVAC/DC Panel labels & feeder names in switchyard at remote substations | Lot | 1
16.4 | VT/CT Marshalling Box | Lot | 1
16.5 | Gas Handling Trolley including accessories | Lot | 1
16.6 | Laptops as desribed in technical specification | No. | 10
16.7 | Mobile phones with usage charges of KES 5,000/- per month per phone | No. | 10
16.8 | CSR project | Lot | 1
16.9 | Tree growing Initiative | Lot | 1
16.10 | CPC 100 Multifunctional Primary Test System | No. | 1
16.11 | CMC 356 Protection system Test System, including RelaySimTest and IEC61850 licenses | No. | 1
16.12 | DANEO 400 Mergin Units tester and Network Analyzer | No. | 1
16.13 | StationScout Test System | No. | 1
16.14 | Portable Earth Leads | Set | 6
16.15 | CCTV system for 400kV & 132kV | Lot | 1
16.16 | All kinds of furnitures as detailed under Item 27.21 of Part-2 , Employers requirement. | Lot | 1
16.17 | Codes and standards as mentioned in the Employer requirements, section 7.1 | Lot | 2
16.18 | Document Management system active upon contract effectiveness until end of Defect liability period | lot | 1
TOTAL PRICE ITEM 16
17 | SITE TRANSPORT, SITE OFFICE AND PERMANENT LIVING ACCOMMODATION, STAFF TRAINING, INTERSHIP COSTS
17.1 | Transport Services and Vehicles
17.1.1 | Transport Services - Vehicle Type 1 | No. | 6
17.1.2 | Vehicle Type 2 | No. | 1
17.2 | Site Office fully furnished as specified in the Employer's Requirements and with fully furnished kitchenettes, Storage Facilities. | Lot | 1
17.3 | Site and staff training as per employer's requirement | Lot | 1
17.3.1 | Training on the Site:
17.3.1.1 | OMICRON CMC 356 Three Phase Secondary Injection Kit complete with 2CMGPS and Two RelaySim Test Software and IEC 61850 license. | Lot | 1
17.3.1.2 | OMICRON DANEO 400 Hybrid network analyzer for testing Mergin Units and communication network | Lot | 1
17.3.1.3 | OMICRON Station Scout, Substation Automation test set | Lot | 1
17.3.1.4 | CPC 100 Multifunctional Primary Test System | Lot | 1
17.3.1.5 | 11kV cable training | Lot | 1
17.3.1.6 | Solar water heating system | Lot | 1
17.3.1.7 | Site Operation and Maintenance Training (20 Engineers for 2 weeks) | Lot | 1
17.3.2 | Training at Contractor Home Office as per Employers Requirements
17.3.2.1 | Protection and Control for Electrical Power Systems (8 Engineers for 2 weeks): | Lot | 1
17.3.2.2 | Power System Analysis (8 Engineers for 2 weeks) | Lot | 1
17.3.2.3 | Substation Electrical Design (8 Engineers for 2 weeks) including softwares supply | Lot | 1
17.3.2.4 | Communication & SCADA– Application & Design (8 Engineers for 2 weeks) | Lot | 1
17.3.2.5 | Civil Engineering Design (8 Engineers for 2 weeks) | Lot | 1
17.3.2.6 | Training on Digital Fault Recorder, Fault Locator and Phasor Measurement unit (PMU)(8 Engineers for 2 weeks) | Lot | 1
17.3.2.7 | Training on Digital substation and Cyber security 2 batches of 8 Engineers per batch for 4 weeks. | Lot | 1
17.3.2.8 | Proposed Internship program for engineering students (shall be approved by KETRACO)-10 students | Lot | 1
17.3.2.9 | Knowledge and skill transfer to local engineers | Lot | 1
17.3.3 | Softwares as decribed in Section 2, Chapter 1 of the Employer's Requirements
17.3.3.1 | AutoCAD for windows - Premium plan subcription including training | No. | 2
17.3.3.2 | AutoCAD for windows with AutoCAD Electrical toolset - premium plan subscritpion including training | No. | 1
17.3.3.3 | PSSE (maintenance and support) including training | No. | 2
17.3.3.4 | PLS CADD (subscription) including training | No. | 3
17.3.5.5 | PLS Tower (subscription) including training | No. | 5
TOTAL PRICE ITEM 17
18 | DESIGN REVIEW MEETING
18.1 | Design review meeting at the Contractor’s home country’s design office as per Employers Requirements | Lot | 1
TOTAL PRICE ITEM 18
19 | MANDATORY SPARE PARTS
19.1 | 400kV Circuit breaker (1 Pole operated -3 phase) Complete with mechanism box , Central Control Panel, complete with operating platform. All accessories will be included to make testing and commissioning completed | No. | 1
19.2 | 132kV Circuit breaker (3 pole/gang operated, 3 phase) Complete with mechanism/central box (with current rating same as bus coupler ). All accessories will be included to make testing and commissioning completed, complete with operating platform. | No. | 1
19.3 | 400 kV Post type current transformer for Protection & Measuring (1-phase) as per TDS All accessories will be included to make testing and commissioning completed. | No. | 3
19.4 | 132 kV Post type current transformer for Protection & Measuring (1-phase) for the OHL feeder as per TDS All accessories will be included to make testing and commissioning completed. | No. | 3
19.5 | 400 kV Post type Capacitive Voltage Transformer for Protection & Measuring (1-phase) as per TDS All accessories will be included to make testing and commissioning completed. | No. | 3
19.6 | 132 kV Post type Capacitive Voltage Transformer for Protection & Measuring (1-phase) as per TDS All accessories will be included to make testing and commissioning completed. Phase summation galvanized junction box will be provided | No. | 3
19.7 | Low Power Instrument Transformer (LPIT), or Optical CT | No. | 1
19.8 | 400kV Line distance Protection relay as per TDS | No. | 1
19.9 | 400kV Line differential Protection relay as per TDS | No. | 1
19.10 | Transformer differential Protection relay as per TDS | No. | 1
19.11 | 400kV bus bar protection relay as per TDS | No. | 1
19.12 | 132kV bus bar protection relay as per TDS | No. | 1
19.13 | Transformer HVC protection relay as per TDS | No. | 1
19.14 | Bay Control Unit used in 400kV substation as per TDS | No. | 1
19.15 | Bay Control Unit used in 132kV substation as per TDS | No. | 1
19.16 | Phasor measurement unit,PMU relay | No. | 1
19.17 | Common Bay control Unit, as per TDS | No. | 1
19.18 | Managed Ethernet switches | No. | 2
19.19 | Power transformer Gaskets | Lot | 1
19.20 | Transformer back up protection relay-HV | No. | 1
19.21 | Transformer back up protection relay-LV | No. | 1
19.22 | Industrial Eth switch 24 ports, PTP capable | No. | 6
19.23 | Industrial Eth switch 8/10 ports, PTP capable | No. | 2
19.24 | Industrial Redbox - 8 ports, PTP and PRP capable | No. | 2
19.25 | Mergin Unit IEC61850/IEC61869-9 | No. | 8
19.26 | Switch Controller Unit SCU | No. | 4
19.27 | Grand Master Clock PTP, PRP capable | No. | 1
19.28 | GPS antenna | No. | 1
19.29 | Firewall: SSL/TSL/SSH/NAT, 6 ports, throughput 1.4 Gbps | No. | 1
19.30 | Gateway Computer | No. | 1
19.31 | Station SCADA Computer | No. | 1
19.32 | one of each telecommunication cards used complete with the terminations, set of long range SFP modules | Lot | 1
19.33 | 2 x 48 core ODF complete with pigtail | Lot | 1
TOTAL PRICE ITEM 19
20 | Factory Acceptance Tests(FAT):
20.1 | Power transformers | LS | 1
20.2 | Earthing/Auxiliary Transformers | LS | 1
20.3 | Shunt reactors | LS | 1
20.4 | Circuit Breakers | LS | 1
20.5 | Disconnector and Earthing switches | LS | 1
20.6 | Instrument Transformers(CT & CVT) | LS | 1
20.7 | Low power Instrument Transformers (LPIT) | LS | 1
20.8 | Surge arrestors | LS | 1
20.9 | Post & Longrod insulators | LS | 1
20.10 | Busbar, Clamps & fittings | LS | 1
20.11 | Equipment steel structures and gantries | LS | 1
20.12 | AC/DC panels, battery chargers | LS | 1
20.13 | Protection, control, Metering, SCU, MU and SCADA system including digital substation | LS | 1
20.14 | Telecommunication equipment | LS | 1
20.15 | Fault monitoring systems/Fault recorder | LS | 1
TOTAL PRICE ITEM 20
TOTAL PRICE SCHEDULE 1 MAKINDU SUBSTATION
Name of the Bidder
Country of origin Declaration Form
Item | Description |  |  |  | Country

## Schedule 3_SS
400/132kV MAKINDU SUBSTATION
Schedules of Rates and Prices
Schedule No. 3
Design Services
Item | Description | Unit | Qty | Unit Price |  | Total Price
|  |  |  | Foreign Currency | Local Currency (KSh) = KENYAN SHILLINGS | Foreign Currency | Local Currency (KSh) = KENYAN SHILLINGS
|  |  | (1) | (2) | (3) | (4)=(1)* (2) | (5)=(1)*(3)
1. | Electrical Design
1.2 | 400kV and 132kV Primary Equipment Design including power transformers and reactors | Lot | 1
1.2 | Insulation Coordination Studies | Lot | 1
1.3 | Substation earthling system design | Lot | 1
1.4 | Lightning Protection Design(shield wires and spikes) | Lot | 1
1.5 | Outdoor/Indoor lighting design | Lot | 1
1.6 | Protection, control, fault monitoring and metering system design, relay settings calculations and studies | Lot | 1
1.7 | LVAC/DC Auxiliary Systems Design including chargers, batteries, panels etc. | Lot | 1
1.8 | Substation automation system (SAS) and IEC61850 system and digital substation design following the method Top-Down | Lot | 1
1.9 | LV cables and accessories | Lot | 1
1.10 | Telecommunication system design including NCC/RCC | Lot | 1
1.11 | Remote end changes and modifications (include all relevant drawings and documents), Contractor shall be required to use the existing hard copies of As Built drawings for modification. Modification of the protection, control, communication, SCADA system, NCC and RCC SCADA will be required. | lot | 1
1.12 | Preliminary testing documents, Final testing documents Final Documents with final inspection and results of all installed equipment ( equipment name, details of equipment, result of testing . Energizing document | lot | 1
1.13 | All other relevant substation electrical works design to ensure a fully functional substation
1.14 | Transient Recovery Voltage (TRV) and transformer energization study
TOTAL PRICE FOR ELECTRICAL WORKS DESIGN
2. | Civil Works design
2.1 | hydrological survey and flood risk assessment and earth work design | Lot | 1
2.2 | Equipment and gantry foundation design
2.3 | Gantry and steel structure design | Lot | 1
2.4 | Buildings including Control Building, guard house, diesel generator, Central Policing Infrastructure Unit Housing (CIPU) and Warehouse design | Lot | 1
2.5 | Internal/External access road, Drainage, sewerage and plumbing works design | Lot | 1
2.6 | HVAC air-conditioning, CCTV and Access Control system design | Lot | 1
2.7 | All other relevant substation civil works design to ensure a fully functional substation including borehole, plumbing, landscaping, parking, perimeter fence etc. | Lot | 1
TOTAL PRICE FOR CIVIL WORKS DESIGN
TOTAL PRICE SCHEDULE 3 MAKINDU SUBSTATION

## Schedule 4_SS
400/132kV MAKINDU SUBSTATION
Schedules of Rates and Prices
Schedule No. 4
Installation and Other Services
Item | Description | Unit | Qty | Unit Price |  | Total Price
|  |  |  | Foreign Currency | Local Currency (KSh) = KENYAN SHILLINGS | Foreign Currency | Local Currency (KSh) = KENYAN SHILLINGS
|  |  | (1) | (2) | (3) | (4)=(1)* (2) | (5)=(1)*(3)
Bidders shall enter a code representing the country of origin of all imported plant and equipment.
Specify currency create and use as many columns for unit price and total price as there are currencies
1 | 400kV PRIMARY PLANT
1.1 | Circuit breaker (1 Pole operated -3 phase) Complete with mechanism box , Central Control Panel, complete with operating platform. All accessories will be included to make testing and commissioning completed . | No. | 12
1.2 | Disconnector, motorized (1 Pole operated-3-phase) with earth mat, Complete with Central Control Panel. All accessories will be included to make testing and commissioning completed. | No. | 24
1.3 | Disconnector, motorized (1 Pole operated-3 phase) complete with one integral motorized earth switch and earth mat, Complete with Central Control Panel. All accessories will be included to make testing and commissioning completed. | No. | 8
1.4 | Surge arrester (1-phase) including surge counter with earth leakage meter connecting to earth greed. All accessories will be included to make testing and commissioning completed. | No. | 24
1.5 | Post insulator -for main busbar, All accessories will be included to make testing and commissioning completed | Lot | 1
1.6 | Post insulator - for bay busbar, All accessories will be included to make testing and commissioning completed | Lot | 1
1.7 | Post insulator - Under-hung All accessories will be included to make testing and commissioning completed | Lot | 1
1.8 | Strain (Longrod)insulator - with turnbuckle All accessories will be included to make testing and commissioning completed | Lot | 1
1.9 | Strain(Longrod) insulator - without turnbuckle All accessories will be included to make testing and commissioning completed. | Lot | 1
1.10 | Post type current transformer for Protection & Measuring (3 Core,1-phase) for lines. All accessories will be included to make testing and commissioning completed. Phase summation galvanized junction box will be provided. | No. | 24
1.11 | Post type current transformer for Protection & Measuring (3 Core,1-phase).for transformers All accessories will be included to make testing and commissioning completed. Phase summation galvanized junction box will be provided. | No. | 12
1.12 | Post type current transformer -High Accuracy Tariff metering (2 Core, 1-phase) All accessories will be included to make testing and commissioning completed. Phase summation galvanized junction box will be provided. | No. | 12
1.13 | Capacitive voltage transformer - (Protection & Measuring, 1-phase) Supply will be based on TDS and description. All accessories will be included to make testing and commissioning completed . Phase summation galvanized junction box will be provided | No. | 20
1.14 | Capacitive Voltage transformer (1-phase) (High Accuracy Metering) Supply will be based on TDS and description. All accessories will be included to make testing and commissioning completed. Phase summation galvanized junction box will be provided. | No. | 12
1.15 | Conductor - Tubular Supply will be based on TDS and description. All accessories will be included to make testing and commissioning completed. | Lot | 1
1.16 | Conductor - Stranded Supply will be based on TDS and description. All accessories will be included to make testing and commissioning completed. | Lot | 1
1.17 | Connectors - Tube ; All accessories will be included to make testing and commissioning completed | Lot | 1
1.18 | Connectors - for Stranded flashover, down-droppers, equipment connect.etc. All accessories will be included to make testing and commissioning completed | Lot | 1
TOTAL PRICE ITEM 1
2 | 132kV PRIMARY PLANT
2.1 | Circuit breaker (3 pole/gang operated, 3 phase) Complete with mechanism/central box ( IBT1 & 2, Bus sections ). All accessories will be included to make testing and commissioning completed, complete with operating platform. | No. | 4
2.2 | Circuit breaker (3 pole/gang operated, 3 phase) Complete with mechanism/central box (for bus coupler ). All accessories will be included to make testing and commissioning completed, complete with operating platform. | No. | 2
2.3 | Circuit breaker (1 pole operated-3 phases) for OHL Complete with mechanism box/Central Control Panel. All accessories will be included to make testing and commissioning completed complete with operating platform | No. | 2
2.4 | Disconnector, motorized (3-phase) with earth math connecting to earth grid(busbar DS for IBT1 & IBT 2 and OHL). All accessories will be included to make testing and commissioning completed | No. | 8
2.5 | Disconnector, motorized (3-phase) with earth math connecting to earth grid(for bus couplers). All accessories will be included to make testing and commissioning completed | No. | 4
2.6 | Disconnector, motorized (3-phase) complete with one integral earth switch(for IBT 1& IBT 2 and OHLs) All accessories will be included to make testing and commissioning completed. Earth mat will be provided connected to earth grid. | No. | 4
2.7 | Disconnector, motorized (3-phase) complete with two integral motorized earth switches(for bus sections) All accessories will be included to make testing and commissioning completed. Earth mat will be provided connected to earth grid. | No | 4
2.8 | Surge arrester (1-phase) including surge counter with earth leakage meter connecting to earth greed All accessories will be included to make testing and commissioning completed. | No. | 12
2.9 | Post insulator - for the main busbar, All accessories will be included to make testing and commissioning completed | Lot | 1
2.10 | Post insulator - for the bay busbar support, All accessories will be included to make testing and commissioning completed | Lot | 1
2.11 | Post insulator - Under-hung All accessories will be included to make testing and commissioning completed | Lot | 1
2.12 | Strain (Longrod) insulator - with turnbuckle All accessories will be included to make testing and commissioning completed | Lot | 1
2.13 | Strain (Longrod) insulator - without turnbuckle All accessories will be included to make testing and commissioning completed | Lot | 1
2.14 | 132kV Post type current transformer for IBT Protection & Metering. (1-phase, 4 cores) with galvanized phase summation junction box. All accessories will be included to make testing and commissioning completed | No. | 6
2.15 | 132kV Post type current transformer for OHL Protection & Metering. (1-phase, 4 cores) with galvanized phase summation junction box. All accessories will be included to make testing and commissioning completed | No. | 6
2.16 | 132kV Post type current transformer, for Bus section and bus coupler (1-phase, 2 cores) with galvanized phase summation junction box. All accessories will be included to make testing and commissioning completed | No. | 24
2.17 | 132kV Capacitive voltage Transformer of Protection & Measuring (1-phase, three cores) for 132kV busbar. All accessories will be included to make testing and commissioning completed. | No | 4
2.18 | 132kV Capacitive voltage transformer - (1-phase, High Accuracy Metering) for protection and metering with galvanized phase summation box. All accessories will be included to make testing and commissioning completed | No. | 12
2.19 | Conductor - Tube - 132kV Bus bar 1&2 - min. 100mm dia All accessories will be included to make testing and commissioning completed | Lot | 1
2.20 | Conductor - Stranded (overfly/down drop and equipment connection) All accessories will be included to make testing and commissioning completed | Lot | 1
2.21 | Connectors - Tube min. 100mm dia (132kv Bus bar) All accessories will be included to make testing and commissioning completed | Lot | 1
2.22 | Connectors - Stranded conductor All accessories will be included to make testing and commissioning completed | Lot | 1
2.23 | Low Power Instrument Transformer (LPIT),or Optical CT with all accessories necessary for complete testing and commissioning | No | 3
TOTAL PRICE ITEM 2
3 | Power Transformer and Busbar Reactor
3.1 | INTERBUS TRANSFORMER (IBT - Three windings)
3.1.1 | Three phase units with three windings 400/132/11kV, 75/90 MVA (ONAN/ONAF) including HV/LV/TV/Neutral CT's & Bushing CTs | No. | 2
3.1.2 | Fire Protection system with Nitrogen Injection & Oil Evacuation System, explosion proof, based on description in Tender document (all accessories including trolley fire extinguisher, sand box , shovels and buckets(at least 2 sets)shall be included to make testing and commissioning completed) | No. | 2
3.1.3 | Power transformer online monitoring system based on description in Tender document (all accessories will be included to make testing and commissioning completed). | No. | 2
3.1.4 | Parallel transformer online operation system using IEC 61850 GOOSE communication and interconnecting in master -follower mode (based on description on description in Tender document ), (all accessories will be included to make testing and commissioning completed). | Lot | 1
3.1.5 | Surge arrester (1-phase), installed in the Power TX11kV cable box | No. | 6
3.2 | Busbar Shunt Reactor
3.2.1 | Three phase units with three windings 400kV, 50MVAR Reactor including HV and Neutral CT's & Bushing CTs | No. | 2
TOTAL PRICE ITEM 3
4 | 400kV PROTECTION SYSTEMS
4.1 | 400kV OHL Protection System (4 sets)
4.1.1 | Main 1 21L Protection (different vendor from Main 2) | No. | 4
4.1.2 | Main 2 87L Protection (different vendor from Main 1) | No. | 4
4.1.3 | Auto-Reclose Protection function (included within Main 1 and Main2) | No. | 4
4.1.4 | Panels including all accessories, e.g. AC/DC system, wiring etc. to make the system complete | Panels (No) | 4
4.1.5 | Phasor Measurement Unit (PMU) including PDC, and accessories required to integrate in KETRACO's SDH network | Lot | 1
4.1.6 | Point on Wave controller | No. | 8
4.2 | 400kV HV Transformer Protection System including (2 sets):
4.2.1 | Main 87T+87N Protection | No. | 2
4.2.2 | Backup 50/51(N) Protection and HV Neutral 51N Stand-by Earth-Fault Protection | No. | 2
4.2.3 | 87HVC1 Connection Protection (different vendor from Main 87HVC2) | No. | 2
4.2.4 | 87HVC2 Connection Protection (different vendor from Main 87HVC1) | No. | 2
4.2.5 | Panels including all accessories, e.g. AC/DC system, wiring etc. to make the system complete | Panels (No) | 4
4.2.6 | Point on Wave controller | No. | 2
4.3 | 400kV HV Busbar Shunt Reactor including (2 sets):
4.3.1 | Main 87R+87NR Protection | No. | 2
4.3.2 | Backup 50/51(N) Protection | No. | 2
4.3.3 | 87HVC1 Connection Protection (different vendor from Main 87HVC2) | No. | 2
4.3.4 | 87HVC2 Connection Protection (different vendor from Main 87HVC1) | No. | 2
4.3.5 | Panels including all accessories, e.g. AC/DC system, wiring etc. to make the system complete | Panels (No) | 2
4.3.6 | Point on Wave controller | No. | 2
4.4 | 400kV Bus bar Protection System 400kV Bus bar Protection (BUS BAR 1 &2 ). All accessories will be included to make testing and commissioning completed. | Lot | 2
4.4.1 | The 50BF function shall be included for CBS as per SLDs | No | 8
4.5 | Modification works in remote substation Rabai or Mariakani & Isinya Substation. Including relay setting & relay configuration etc. | Lot | 1
4.6 | Miscellaneous modification works as necessary to make the complete 400kV protection system functional | Lot | 1
4.7 | Update the remote substations drawings (Rabai/Mariakani and Isinya) | Lot | 1
TOTAL PRICE ITEM 4
5 | 132kV PROTECTION SYSTEMS
5.1 | 132kV OHL Protection System including: | Lot | 2
5.1.1 | Main 1 21L Protection (different vendor from Main 2) | No. | 2
5.1.2 | Main 2 87L Protection (different vendor from Main 1) | No. | 2
5.1.3 | Auto-Reclose Protection function (included within Main 1 and Main2) | No. | 2
5.1.4 | Panels including all accessories, e.g. AC/DC system, wiring etc. to make the system complete | Panels (No) | 2
5.1.5 | Modification works at the remote end substations from Makindu substation including relay setting calculations & relay configuration & testing. | lot | 1
5.2 | 132kV LV Transformer Protection System including: | Lot | 2
5.2.1 | Backup 50/51(N),67/67N Protection, LV NEUTRAL, 51N, LV REF, LVSBEF | No. | 2
5.2.2 | Earthing Transformer 11kV side-87N/TV, 11kV side standby earth fault protection 51NTV, 50/51, TV REF and BCU | No. | 2
5.2.3 | The AVR Panel including all accessories including AVR, AVR relay, wiring etc. to make the system completes. (one panel for both) | Panels (No) | 2
5.2.4 | Panels including all accessories, e.g. AC/DC system, wiring etc. to make the system complete | Panels (No) | 2
5.3 | 132kV complete Bus bar Protection System - OHL Bus bar protections - TR bus bar protections - Bus coupler Bus bar protection - Bus section Bus bar protection - Bus bar panels | Lot | 1
5.4 | 132kV Protection - Bus coupler protection (integrated with BCU) - Bus section protection (integrated with BCU) - Bus coupler & Bus section shared panel | Lot | 2
5.5 | Miscellaneous modification works as necessary to make the complete 132kV protection system functional | Lot | 1
TOTAL PRICE ITEM 5
6 | 400/132kV SUBSTATION AUTOMATION SYSTEM
6.1 | 400/132kV Bay Control Units and panels: | Lot | 2
6.1.1 | Bay Control Units (BCU) 400kV (full diameters) - One BCU per CB. include 25 and VSL function - BCU for CB-Bus-OHL - BCU for CB-TIE include 50BF function - BCU for CB-Bus-Tx | Lot | 2
6.1.2 | Bay Control Units (BCU) 400kV (full diameters) - One BCU per CB. include 25 and VSL function - BCU for CB-Bus-OHL - BCU for CB-TIE include 50BF function - BCU for CB-Bus-Reactor | Lot | 2
6.1.3 | Bay Control Units (BCU) 132kV - One BCU per CB. include 25 and VSL function - BCU for OHL - BCU for Coupler (C&P combined ) - BCU for Bus-Section (C&P combined) - BCU for each Transformer feeder | Lot | 1
6.1.4 | Bay Control Panels - 400kV one panel per diameter - 132kV C&P combined in the same panel | Lot | 1
6.1.5 | Auxiliary and Common Services Bay Control Units BCUs, one per each Earthing Transformer 11/0.415kV, including 415V side-51N protection. Including one combined panel for both | Lot | 1
6.2 | 400/132kV Local Area Network: | Lot | 2
6.2.1 | PRP Process Bus Network composed of both LAN-A and LAN-B, 1000BaseFX, industrial Eth switches, PTP capable (technical requirements in Appendix), Physically independent thus: - PRP LAN A & LAN B, 400kV Diameter 1 - PRP LAN A & LAN B, 400kV Diameter 2 - PRP LAN A & LAN B, 400kV Diameter 3 - PRP LAN A & LAN B, 400kV Diameter 4 - PRP LAN A & LAN B, 132kV for two OHL bays - PRP LAN A & LAN B, 132kV for two Transformer bays - PRP LAN A & LAN B, 132kV for two couplers and two bus section bays Switches to be installed in the control cabinets of the corresponding bay | Lot | 1
6.2.2 | PRP Station Bus Network composed of both LAN-A and LAN-B, 100BaseFX, industrial Eth switches, PTP capable (technical requirements in Appendix) | Lot | 1
6.2.3 | PRP Process Bus Inter-bay Network composed of both LAN-A and LAN-B, 1000BaseFX, industrial Eth switches, PTP capable (technical requirements in Appendix), Physically independent thus | Lot | 1
6.2.4 | PRP Redboxes, 100BaseFX, PTP capable (technical requirements in Appendix), minimum 8 ports | Lot | 4
6.2.5 | RSTP DMZ Network, 100BaseTx, PTP capable (technical requirements in Appendix) | Lot | 1
6.2.6 | Outdoor armored Fiber optics and Fiber Optic Organizer for connections from the Marshaling Kiosks to the control room | Lot | 1
6.2.7 | Armed Fiber optics, patch cords FO, Patch cords Eth and other wiring necessary for the Network | Lot | 1
6.3 | Firewall: SSL/TSL/SSH/NAT, 6 ports, throughput 1.4 Gbps (technical requirements in Appendix) | Lot | 1
6.4 | Cybersecurity Intrution Detection and Functional Monitoring System | Lot | 2
6.5 | Human Machine Interface (OWS) | Lot | 2
6.6 | Engineering Workstation (EWS) | No. | 2
6.7 | SCADA servers | No. | 2
6.8 | Gateways | No. | 2
6.9 | Time synchronization system including clocks, antennas and accessories (see technical requirements in Digital substation Appendix) | No. | 2
6.10 | Laser Jet printer (A3 & A4) | No. | 1
6.11 | General Purpose Printer | No. | 1
6.12 | 400/132kV Digital interfaces: | Lot | 2
6.12.1 | Marshalling Kiosks for each 400kV Bus-side CB, including: - 3 MUs and their test terminal blocks - 2 SCUs - Fiber Optic Organizer - AC/DC and other Auxiliary systems Combination of MUs/SCUs are possible based on the Digital substation Appendix | Lot | 8
6.12.2 | Marshalling Kiosks for each 400kV Tie CB full-diameters, including: - 2 MUs and their test terminal blocks - 2 SCUs - Fiber Optic Organizer - AC/DC and other Auxiliary systems Combination of MUs/SCUs are possible based on the Digital substation Appendix | Lot | 4
6.12.3 | Marshalling Kiosks for each Power Transformer 400/132/11kV, including: - 5 MUs and their test terminal blocks (consider the accuracy required for ground CTs) - 1 SCUs (only inputs required) - Fiber Optic Organizer - AC/DC and other Auxiliary systems Combination of MUs/SCUs are possible based on the Digital substation Appendix | Lot | 2
6.12.4 | Marshalling Kiosks for each 400kV-50MVAR shunt reactor, including: - 3 MUs and their test terminal blocks (consider the accuracy required for ground CTs) - 1 SCUs (only inputs required) - Fiber Optic Organizer - AC/DC and other Auxiliary systems Combination of MUs/SCUs are possible based on the Digital substation Appendix | Lot | 2
6.12.5 | Marshalling Kiosks for each 132kV OHL with LPIT CT, including: - 1 Stand Alone MUs and their test terminal blocks - 1 MU as part of the LPIT and their test terminal blocks - 2 SCUs - Fiber Optic Organizer - AC/DC and other Auxiliary systems Combination of MUs/SCUs are possible based on the Digital substation Appendix | Lot | 2
6.12.6 | Marshalling Kiosks for each 132kV OH without LPIT CT, including: - 2 Stand Alone MUs and their test terminal blocks - 2 SCUs - Fiber Optic Organizer - AC/DC and other Auxiliary systems Combination of MUs/SCUs are possible based on the Digital substation Appendix | Lot | 2
6.12.7 | Marshalling Kiosks for each 132kV Transformer feeder, including: - 2 MUs and their test terminal blocks - 2 SCUs - Fiber Optic Organizer - AC/DC and other Auxiliary systems Combination of MUs/SCUs are possible based on the Digital substation Appendix | Lot | 2
6.12.8 | Marshalling Kiosks for each 132kV coupler or bus section (combining MKs might be possible based on distances), including: - 2 MUs and their test terminal blocks - 1 SCUs - Fiber Optic Organizer - AC/DC and other Auxiliary systems Combination of MUs/SCUs are possible based on the Digital substation Appendix | Lot | 4
TOTAL PRICE ITEM 6
7 | TELECOMMUNICATION & NCC/RCC
7.1 | New Telecommunication System for 400/132kV Substation. | Lot | 1
7.2 | New Tele protection Signaling Equipment for 400/132kV Substation. | Lot | 1
7.3 | New IP PABX and Telephone Equipment for 400/132kV Substation. | Lot | 1
7.4 | Incorporate new and modified substation equipment into the SCADA/EMS System at the NCC/RCC. | Lot | 1
7.5 | Modifications to NCC/RCC databases and applications | Lot | 1
7.6 | Update of the Geographic Map | Lot | 1
7.7 | Modifications to NCC/RCC operator displays | Lot | 1
7.8 | Modifications to NCC/RCC mimic board | Lot | 1
7.9 | Modification of Remote end Substation Telecommunication System | Lot | 1
TOTAL PRICE ITEM 7
8 | LV CABLES AND ACCESSORIES
8.1 | Auxiliary power and control cabling | Lot | 1
8.2 | Substation internal fibre optic cabling | Lot | 1
8.3 | Cabling installation hardware e.g. cable tray supports, cable trays, fixing hardware, glands, lugs, fire proof sealing of ducts/conduits/openings etc. | Lot | 1
TOTAL PRICE ITEM 8
9 | EARTHING & LIGHTNING PROTECTION
9.1 | Earthing system | Lot | 1
9.2 | Potable Earth leads | Set | 2
9.3 | Lightning protection system | Lot | 1
TOTAL PRICE ITEM 9
10 | 11KV CABLE SYSTEM
10.1 | 11kV cable system for connection between IBT and Earthing/auxiliary transformer | Lot | 2
10.2 | Cabling installation hardware e.g. cable trays etc. | Lot | 2
TOTAL PRICE ITEM 10
11 | SUPPORT STRUCTURES
11.1 | Steel supports for 400kV equipment including all accessories | Lot | 1
11.2 | Steel supports for 132kV equipment including all accessories | Lot | 1
11.3 | Gantries and other structures within substation | Lot | 1
11.4 | Structures for interconnecting 400kV and 132kV switchyards | Lot | 1
TOTAL PRICE ITEM 11
12 | CIVIL WORKS
12.1 | Hydrological and topographical site survey (based on substation layout dimension and dimension of allocated land) | Lot | 1
12.2 | Site clearance like removal of shrubs, bushes, vegetation, buildings, foundations as necessary | Lot | 1
12.3 | Earth works including excavation, backfilling and excavation in rock up to a depth of 2m | Lot | 1
12.4 | Soil Investigation | Lot | 1
12.5 | Temporary works | Lot | 1
12.6 | Grading and landscaping on completion | Lot | 1
12.7 | Surfacing with gravel | Lot | 1
12.8 | Switchyard internal Roads | Lot | 1
12.9 | Substation Drainage system | Lot | 1
12.10 | Sewage system | Lot | 1
12.11 | Water supply system including borehole | Lot | 1
12.12 | Substation land perimeter chain link fence including security for watch and ward during construction phase ( based on proposed substation layout) | m | approx. 1350
12.13 | Switchyard chain link fence | Lot | 1
12.14 | Substation gate | Lot | 1
12.15 | Cable trenching / ducts with cable trays for cable trenches | Lot | 1
12.16 | Substation road lighting | Lot | 1
12.17 | Substation compound lighting | Lot | 1
12.18 | Substation guard house & Telecom collocation room including building services e.g. Lighting, Small Power System, HVAC, Fire Detection, based on drawing and description
12.18.1 | Guard House Civil and Structural Works | Lot | 1
12.18.2 | Small power and electrical building services | Lot | 1
12.18.3 | HVAC and air conditioning | Lot | 1
12.18.4 | Internal lighting | Lot | 1
12.18.5 | Fire detection system | Lot | 1
12.18.6 | Drainage and Plumbing system | Lot | 1
12.18.7 | Access control system | Lot | 1
12.19 | Substation Control building including building services (e.g. Lighting, Small Power System, HVAC, Fire Detection), Eyewash facility and access control system.
12.19.1 | Control Building Civil and Structural Works | Lot | 1
12.19.2 | Small power and electrical building services | Lot | 1
12.19.3 | HVAC and air conditioning | Lot | 1
12.19.4 | Internal lighting | Lot | 1
12.19.5 | Fire detection system | Lot | 1
12.19.6 | Drainage and Plumbing system | Lot | 1
12.19.7 | Access control system | Lot | 1
12.20 | Covered Car parking for Control Building | Lot | 1
12.21 | Central Policing Infrastructure Unit Housing (CIPU) units including building services (e.g. Lighting, Small Power System, HVAC, Fire Detection)
12.21.1 | Central Policing Infrastructure Unit Housing (CIPU) units Civil and Structural Works | Lot | 4
12.21.2 | Small power and electrical building services | Lot | 4
12.21.3 | HVAC and air conditioning | Lot | 4
12.21.4 | Internal lighting | Lot | 4
12.21.5 | Fire detection system | Lot | 4
12.21.6 | Drainage and Plumbing system | Lot | 4
12.21.7 | Access control system | Lot | 4
12.21.8 | Chain link fence surrounding CIPU units | Lot | 1
12.22 | Warehouse including building services (e.g. Lighting, Small Power System, HVAC, Fire Detection) and also open storage area
12.22.1 | Warehouse Civil and Structural Works | Lot | 1
12.22.2 | Small power and electrical building services | Lot | 1
12.22.3 | HVAC and air conditioning | Lot | 1
12.22.4 | Internal lighting | Lot | 1
12.22.5 | Fire detection system | Lot | 1
12.22.6 | Drainage and Plumbing system | Lot | 1
12.22.7 | Access control system | Lot | 1
12.22.8 | Civil works for Open storage area including chain link fence | Lot | 1
12.22.9 | Overhead crane system including but not limited to supply, installation and commissioning with all associated associated accessories. | Lot | 1
12.23 | Diesel generator house based on dimension of generator along with generator house/building.
12.23.1 | Diesel generator units Civil and Structural Works | Lot | 1
12.23.2 | Small power and electrical building services | Lot | 1
12.22.3 | HVAC and air conditioning | Lot | 1
12.23.4 | Internal lighting | Lot | 1
12.23.5 | Fire detection system | Lot | 1
12.23.6 | Drainage and Plumbing system | Lot | 1
12.23.7 | Access control system | Lot | 1
12.24 | Foundation for 400kV equipment/support/gantries structures | Lot | 1
12.25 | Foundation for 132kV equipment/support/gantries structures | Lot | 1
12.26 | Foundation for Water tank, CCTV camera poles, covered car park and other equipment within the substation | Lot | 1
12.27 | Foundation for Structures for interconnecting 400kV and 132kV switchyards | Lot | 1
12.28 | Miscellaneous foundation to complete the requirements of work | Lot | 1
12.29 | IBT Plinth and oil containment tank | Set | 2
12.29.1 | IBT oil separation tank for two transformers complete | No. | 1
12.30 | Plinth and oil containment tank for busbar reactor | Set | 2
12.31 | Earthing/Auxiliary Transformer Plinth and oil containment tank. | Set. | 2
12.32 | Firewalls between two transformers and two reactors | Lot | 1
12.33 | Water system with automatic controls as detailed in clause 41.33.7.1.2 | Lot | 1
12.34 | Substation asphalt access/approach road from the Makindu substation to Mombasa road complete with drainage facilities and culverts as necessary. | km | Approx. 6
TOTAL PRICE ITEMS 12
13 | AUXILIARY SUPPLY
13.1 | Control building LVAC system based on drawings including two AC panels with bus sections with CB and detection of voltage. It will be provided connection to ET1, ET2 and generator with automatic changeover and interlocking. The LVAC panel should have meters with CL 0.2 for the incomers from Auxiliary/Earthing transformers | Lot | 1
13.2 | 110VDC System Control Building
13.2.1 | 110VDC Distribution board with auto changeover in main control building | Lot | 1
13.2.2 | 110VDC Chargers in main control building | Lot | 1
13.2.3 | 110VDC batteries in main control building | Lot | 1
13.3 | 48VDC System Control Building
13.3.1 | 48VDC Distribution board with auto changeover in main control building | Lot | 1
13.3.2 | 48VDC Chargers in main control building | Lot | 1
13.3.3 | 48VDC batteries in main control building | Lot | 1
13.4 | 415V Inverter system, minimum 4KVA including inverters, static switch, manual bypass switch & distribution panels | Lot | 1
13.5 | Earthing (Auxiliary) transformer 11/0.415kV, 500kVA - for whole substation | No. | 2
13.6 | Diesel Generator 250kVA including generator control and protection panel for whole substation | No. | 1
TOTAL PRICE ITEM 13
14 | TARIFF METERING
14.1 | Tariff metering panel for 400kV OHL feeders, complete with wiring, accessories etc. and including: | Lot | 2
14.1.1 | Main Meter | No. | 4
14.1.2 | Check Meter | No. | 4
14.2 | Tariff metering panel for 132kV OHL feeders complete with wiring, accessories etc. | Lot | 1
14.2.1 | Main Meter | No. | 2
14.2.2 | Check Meter | No. | 2
14.3 | Tariff metering panel for 132kV transformer incomer feeders complete with wiring, accessories etc. | Lot | 1
14.3.1 | Main Meter | No. | 2
14.3.2 | Check Meter | No. | 2
TOTAL PRICE ITEM 14
15 | FAULT/RECORDING MONITORING SYSTEM
15.1 | Fault Monitoring Panel including:
15.1.1 | Data Acquisition Units Signals inputs via IEC61850 SV and GOOSE | Lot | 1
15.1.2 | Master Station | No. | 1
15.1.3 | Local HMI | No. | 1
15.1.4 | Printer | No. | 1
TOTAL PRICE ITEM 15
16 | MISCELLANEOUS
16.1 | Padlocks / Keys (Access control system for Control building ) | Lot | 1
16.2 | Equipment labels, safety warning plates, road signage's, room name plates etc. | Lot | 1
16.3 | Protection and control panel labels, relay labels, LVAC/DC Panel labels & feeder names in switchyard at remote substations | Lot | 1
16.4 | VT/CT Marshalling Box | Lot | 1
16.5 | Gas Handling Trolley including accessories | Lot | 1
16.6 | Laptops as desribed in technical specification | No. | 10
16.7 | Mobile phones with usage charges of KES 5,000/- per month per phone | No. | 10
16.8 | CSR project | Lot | 1
16.9 | Tree growing Initiative | Lot | 1
16.10 | CPC 100 Multifunctional Primary Test System | No. | 1
16.11 | CMC 356 Protection system Test System, including RelaySimTest and IEC61850 licenses | No. | 1
16.12 | DANEO 400 Mergin Units tester and Network Analyzer | No. | 1
16.13 | StationScout Test System | No. | 1
16.14 | Portable Earth Leads | Set | 6
16.15 | CCTV system for 400kV & 132kV | Lot | 1
16.16 | All kinds of furnitures as detailed under Item 27.21 of Part-2 , Employers requirement. | Lot | 1
16.17 | Codes and standards as mentioned in the Employer requirements, section 7.1 | Lot | 2
16.18 | Document Management system active upon contract effectiveness until end of Defect liability period | lot | 1
TOTAL PRICE ITEM 16
17 | SITE TRANSPORT, SITE OFFICE AND PERMANENT LIVING ACCOMMODATION, STAFF TRAINING, INTERSHIP COSTS
17.1 | Transport Services and Vehicles
17.1.1 | Transport Services - Vehicle Type 1 | No. | 6
17.1.2 | Vehicle Type 2 | No. | 1
17.2 | Site Office fully furnished as specified in the Employer's Requirements and with fully furnished kitchenettes, Storage Facilities. | Lot | 1
17.3 | Site and staff training as per employer's requirement | Lot | 1
17.3.1 | Training on the Site:
17.3.1.1 | OMICRON CMC 356 Three Phase Secondary Injection Kit complete with 2CMGPS and Two RelaySim Test Software and IEC 61850 license. | Lot | 1
17.3.1.2 | OMICRON DANEO 400 Hybrid network analyzer for testing Mergin Units and communication network | Lot | 1
17.3.1.3 | OMICRON Station Scout, Substation Automation test set | Lot | 1
17.3.1.4 | CPC 100 Multifunctional Primary Test System | Lot | 1
17.3.1.5 | 11kV cable training | Lot | 1
17.3.1.6 | Solar water heating system | Lot | 1
17.3.1.7 | Site Operation and Maintenance Training (20 Engineers for 2 weeks) | Lot | 1
17.3.2 | Training at Contractor Home Office as per Employers Requirements
17.3.2.1 | Protection and Control for Electrical Power Systems (8 Engineers for 2 weeks): | Lot | 1
17.3.2.2 | Power System Analysis (8 Engineers for 2 weeks) | Lot | 1
17.3.2.3 | Substation Electrical Design (8 Engineers for 2 weeks) including softwares supply | Lot | 1
17.3.2.4 | Communication & SCADA– Application & Design (8 Engineers for 2 weeks) | Lot | 1
17.3.2.5 | Civil Engineering Design (8 Engineers for 2 weeks) | Lot | 1
17.3.2.6 | Training on Digital Fault Recorder, Fault Locator and Phasor Measurement unit (PMU)(8 Engineers for 2 weeks) | Lot | 1
17.3.2.7 | Training on Digital substation and Cyber security 2 batches of 8 Engineers per batch for 4 weeks. | Lot | 1
17.3.2.8 | Proposed Internship program for engineering students (shall be approved by KETRACO)-10 students | Lot | 1
17.3.2.9 | Knowledge and skill transfer to local engineers | Lot | 1
17.3.3 | Softwares as decribed in Section 2, Chapter 1 of the Employer's Requirements
17.3.3.1 | AutoCAD for windows - Premium plan subcription including training | No. | 2
17.3.3.2 | AutoCAD for windows with AutoCAD Electrical toolset - premium plan subscritpion including training | No. | 1
17.3.3.3 | PSSE (maintenance and support) including training | No. | 2
17.3.3.4 | PLS CADD (subscription) including training | No. | 3
17.3.5.5 | PLS Tower (subscription) including training | No. | 5
17 | TOTAL PRICE ITEM 17
18 | DESIGN REVIEW MEETING
18.1 | Design review meeting at the Contractor’s home country’s design office as per Employers Requirements | Lot | 1
TOTAL PRICE ITEM 18
19 | MANDATORY SPARE PARTS
19.1 | 400kV Circuit breaker (1 Pole operated -3 phase) Complete with mechanism box , Central Control Panel, complete with operating platform. All accessories will be included to make testing and commissioning completed | No. | 1
19.2 | 132kV Circuit breaker (3 pole/gang operated, 3 phase) Complete with mechanism/central box (with current rating same as bus coupler ). All accessories will be included to make testing and commissioning completed, complete with operating platform. | No. | 1
19.3 | 400 kV Post type current transformer for Protection & Measuring (1-phase) as per TDS All accessories will be included to make testing and commissioning completed. | No. | 3
19.4 | 132 kV Post type current transformer for Protection & Measuring (1-phase) for the OHL feeder as per TDS All accessories will be included to make testing and commissioning completed. | No. | 3
19.5 | 400 kV Post type Capacitive Voltage Transformer for Protection & Measuring (1-phase) as per TDS All accessories will be included to make testing and commissioning completed. | No. | 3
19.6 | 132 kV Post type Capacitive Voltage Transformer for Protection & Measuring (1-phase) as per TDS All accessories will be included to make testing and commissioning completed. Phase summation galvanized junction box will be provided | No. | 3
19.7 | Low Power Instrument Transformer (LPIT), or Optical CT | No. | 1
19.8 | 400kV Line distance Protection relay as per TDS | No. | 1
19.9 | 400kV Line differential Protection relay as per TDS | No. | 1
19.10 | Transformer differential Protection relay as per TDS | No. | 1
19.11 | 400kV bus bar protection relay as per TDS | No. | 1
19.12 | 132kV bus bar protection relay as per TDS | No. | 1
19.13 | Transformer HVC protection relay as per TDS | No. | 1
19.14 | Bay Control Unit used in 400kV substation as per TDS | No. | 1
19.15 | Bay Control Unit used in 132kV substation as per TDS | No. | 1
19.16 | Phasor measurement unit,PMU relay | No. | 1
19.17 | Common Bay control Unit, as per TDS | No. | 1
19.18 | Managed Ethernet switches | No. | 2
19.19 | Power transformer Gaskets | Lot | 1
19.20 | Transformer back up protection relay-HV | No. | 1
19.21 | Transformer back up protection relay-LV | No. | 1
19.22 | Industrial Eth switch 24 ports, PTP capable | No. | 6
19.23 | Industrial Eth switch 8/10 ports, PTP capable | No. | 2
19.24 | Industrial Redbox - 8 ports, PTP and PRP capable | No. | 2
19.25 | Mergin Unit IEC61850/IEC61869-9 | No. | 8
19.26 | Switch Controller Unit SCU | No. | 4
19.27 | Grand Master Clock PTP, PRP capable | No. | 1
19.28 | GPS antenna | No. | 1
19.29 | Firewall: SSL/TSL/SSH/NAT, 6 ports, throughput 1.4 Gbps | No. | 1
19.30 | Gateway Computer | No. | 1
19.31 | Station SCADA Computer | No. | 1
19.32 | one of each telecommunication cards used complete with the terminations, set of long range SFP modules | Lot | 1
19.33 | 2 x 48 core ODF complete with pigtail | Lot | 1
TOTAL PRICE ITEM 19
20 | Factory Acceptance Tests(FAT):
20.1 | Power transformers | LS | 1
20.2 | Earthing/Auxiliary Transformers | LS | 1
20.3 | Shunt reactors | LS | 1
20.4 | Circuit Breakers | LS | 1
20.5 | Disconnector and Earthing switches | LS | 1
20.6 | Instrument Transformers(CT & CVT) | LS | 1
20.7 | Low power Instrument Transformers (LPIT) | LS | 1
20.8 | Surge arrestors | LS | 1
20.9 | Post & Longrod insulators | LS | 1
20.10 | Busbar, Clamps & fittings | LS | 1
20.11 | Equipment steel structures and gantries | LS | 1
20.12 | AC/DC panels, battery chargers | LS | 1
20.13 | Protection, control, Metering, SCU, MU and SCADA system including digital substation | LS | 1
20.14 | Telecommunication equipment | LS | 1
20.15 | Fault monitoring systems/Fault recorder | LS | 1
TOTAL PRICE ITEM 20
TOTAL PRICE SCHEDULE 1 MAKINDU SUBSTATION
Name of the Bidder
Country of origin Declaration Form
Item | Description |  |  |  | Country

## Schedule 5_SS
400/132kV MAKINDU SUBSTATION
Schedules of Rates and Prices
Schedule No. 5
Grand Summary
Item | Description | Total Price
|  | Foreign Currency | Local Currency (KSh) = KENYAN SHILLINGS
1 | Total of Schedule No. 1 MAKINDU SS Plant, Equipment and Mandatory Spare Parts Supplied from Abroad
2 | Total of Schedule No. 2 MAKINDU SS Plant, Equipment and Mandatory Spare Parts Supplied from within Employer's Country
3 | Total of Schedule No. 3 MAKINDU SS Design Services
4 | Total of Schedule No. 4 MAKINDU SS Installation and other Services
5
TOTAL PRICES MAKINDU SUBSTATION (SCHEDULES 1-4)

## Schedule 6_SS
400/132kV MAKINDU SUBSTATION
Schedules of Rates and Prices
Schedule No. 6
Recommended/Optional Spare Parts
Item | Description | Unit | Qty | Unit Price |  | Total Price
|  |  |  | Foreign Currency | Local Currency (KSh) = KENYAN SHILLINGS | Foreign Currency | Local Currency (KSh) = KENYAN SHILLINGS
|  |  | (1) | (2) | (3) | (4)=(1)* (2) | (5)=(1)*(3)
The bidder shall list the recommended spare parts required as per the technical specification

## Schedule SS and OHL
400/132kV MAKINDU SUBSTATION AND LILO WORKS
Schedules of Rates and Prices
Grand Summary for Makindu Substation and LILO Works
Item | Description | Total Price
|  | Foreign Currency | Local Currency (KSh) = KENYAN SHILLINGS
1 | Total price for construction of Makindu substation(schedule no. 5, Makindu SS part)
2 | Total price for construction of 400kV and 132kV LILO works(schedule no. 5, Makindu LILO part)
TOTAL PRICES